## Skilled Labour
|  |  | Scope of Work | Header |  |  |  | Target Cost Estimate (19/2/26) |  |  |  | Adjusted Target Cost Estimate |  |  |  | Contract Execution
Service Order Number/Release | Work Order and Work Order Task Combined | Scope No. | Unit 2 2026 Turbine Scope Development - Activity description | Scope Type | Task responsibility (Contractor/ NRGGOS/ Others) | Variable Scope Measurement Definition | Comment | Estimated Hours | Gang rate $/hr | Estimated Total Cost | Notes | Estimated Hours | Gang rate $/hr | Estimated Total Cost (excl.GST) | Notes | Week 1 - Actual Hours | Week 1 - Actual Total Cost | Week 2 - Actual Hours | Week 2 - Actual Total Cost | Week 3 - Actual Hours | Week 3 - Actual Total Cost | Week 4 - Actual Hours | Week 4 - Actual Total Cost | Week 5 - Actual Hours | Week 5 - Actual Total Cost | Week 6 - Actual Hours | Week 6 - Actual Total Cost | Week 7 - Actual Hours | Week 7 - Actual Total Cost | Week 8 - Actual Hours | Week 8 - Actual Total Cost | Week 9 - Actual Hours | Week 9 - Actual Total Cost | Week 10 - Actual Hours | Week 10 - Actual Total Cost | Week 11 - Actual Hours | Week 11 - Actual Total Cost | Variation Hours | Variation Amount | Total - Actual Hours | Total - Actual Total Cost | Total - Actual Gang Rate | Percentage of Hours Complete | Percentage of Cost Used | Task Complete | Forecast Cost for Completion of Project
00173164/00001 | 28243980 | HP - 8.52.6 | HP Dismantling (Refer to 7.2.1 and 7.2.2 of Scope of Works) | H |  |  |  | 363 | 140.1085 | 50859.3738
00173164/00001 | 28243980-04 | 8.52.6.005 | Remove casing to bearing pedestal keys (this task to be discussed with NRG Engineering before removal) | F | Contractor |  | In 2026 Overhaul | 90 | 140.1085 | 12609.7621 |  |  |  | 0
00173164/00001 | 28243980-05 | 8.52.6.011 | Install shaft raising equipment and support the HP and IP rotors | F | Contractor |  | In 2026 Overhaul | 28 | 140.1085 | 3923.0371 |  |  |  | 0
00173164/00001 | 28243980-14 | 8.52.6.155 | Install the radial and axial bearing/pedestal/casing keys | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  | 0
00173164/00001 | 28243980-15 | 8.52.6.159 | Check HP Shaft to pedestal measurements (radial measurements to be compared to last Overhaul records) | F | Contractor |  | In 2026 Overhaul | 16 | 140.1085 | 2241.7355 |  |  |  | 0
00173164/00001 | 28243980-17 | 8.52.6.162 | Engage HP-IP & IP-LP Spiggots, install temporary bolts | O | Contractor |  | This task is not in current scope for 2026, as we are not splitting the HP,IP and LP front to be performed only by Principal Superintendant approval) | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243980-18 | 8.52.6.163 | Install Axial Keys on HP Turbine & Set | F | Contractor |  |  | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00001 | 28243980-19 | 8.52.6.164 | Check Axial Position of HP, IP & LP Turbine | F | Contractor |  |  | 12 | 140.1085 | 1681.3016 |  |  |  | 0
00173164/00001 | 28243986-31 | 8.52.6.200 | Perform coupling alignment of the HP/IP, IP/LP rotors | O | Contractor |  | Only if required. | 21 | 140.1085 | 2942.2778 |  |  |  | 0
00173164/00001 |  |  | Fit coupling bolts HP-IP & IP-LP | O | Contractor |  | Not in current 2026 scope | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 |  |  | Tighten HP/IP coupling including concentricity checks | O | Contractor |  | Not in current 2026 scope | 21 | 140.1085 | 2942.2778 |  |  |  | 0
00173164/00001 |  |  | Tighten IP/LP coupling including concentricity checks | O | Contractor |  | Not in current 2026 scope | 21 | 140.1085 | 2942.2778 |  |  |  | 0
00173164/00001 |  |  | Fit windage plates to the couplings | O | Contractor |  | Not in current 2026 scope | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243980-25 | 8.52.6.169 | Perform Axial Bump Test (all coupled total float) | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243980-26 | 8.52.6.171 | Remove Number 2 and fit thrust pads and perform thrust clearance check | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243980-27 | 8.52.6.172 | Install and perform run out on Stub Shaft | F | Contractor |  | In 2026 Overhaul | 6 | 140.1085 | 840.6508 |  |  |  | 0
00173164/00001 | 28243980-28 | 8.52.6.201 | Install the main oil pump including alignments, etc. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694
00173164/00001 | 28243980-29 | 8.52.6.173 | Adjust casings axial setting for positive and negative clearances, grind keys and fit | F | Contractor |  | In 2026 Overhaul | 21 | 140.1085 | 2942.2778 |  |  |  | 0
00173164/00001 | 28243980-30 | 8.52.6.174 | Initial Rollout Check IP & HP Turbine | O | Contractor |  | This scope is only required if changes are needed due to Turbine shaft to bearing pedestal measurements being different. Please put hours in the TCE to reflect this in case this task is performed. | 24 | 140.1085 | 3362.6032 |  |  |  | 0
00173164/00001 | 28243986-52 | 8.52.6.178 | Turbine on barring | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  | 0
00173164/00001 | 28243983 | IP - 8.53.6 | IP Turbine (Refer to 7.7 in Scope of Work) | H |  |  |  | 40 | 140.1085 | 5604.3387
00173164/00001 | 28243983-02 | 8.53.6.004 | Remove the radial and axial keys (IP casing to bearing pedestals) check clearances are within specfication. | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243983 | LP - 8.54.6 | LP Rotor | H |  |  |  | 51 | 140.1085 | 7145.5319
00173164/00001 | 28243983-03 | 8.54.6.028 | Measure and record reference data as required to determine the correct procedure for reassembly. | F | Contractor |  |  | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243983-04 | 8.54.6.029 | Measure and record rotor in relationship to pedestal, compare figures to 2019 outage. | F | Contractor |  |  | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243983-05 | 8.54.6.030 | Clean and inspect coupling faces. | F | Contractor |  |  | 11 | 140.1085 | 1541.1931 |  |  |  | 0
00173164/00001 | 28243984-01 | 8.54.6.031 | Check hood spray piping nozzles, supports, bled steam drains and unions. | F | Contractor |  |  | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243984-02 | 8.54.6.032 | Replacement of LP outer hood bursting discs (4 off). | F | Contractor |  |  | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243984-04 | 8.54.6.048 | Clean, measure and record all key fits. | F | Contractor |  |  | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243984-07 | 8.54.6.049 | Visual inspection & report on the LP glands | F | Contractor |  |  | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00003 | 28243981 | HPVS1 - 8.55.6 | HP Stop Valve No. 1 | H |  |  |  | 195 | 140.1085 | 27321.1512
00173164/00003 | 28243981-05 | 8.55.6.001 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-06 | 8.55.6.002 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-07 | 8.55.6.003 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  | 0
00173164/00003 | 28243981-08 | 8.55.6.004 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-09 | 8.55.6.005 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-10 | 8.55.6.006 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  | 0
00173164/00003 | 28243981 | HPVS2 - 8.55.6 | HP Stop Valve No. 2 | H |  |  |  | 195 | 140.1085 | 27321.1512
00173164/00003 | 28243981-11 | 8.55.6.007 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-12 | 8.55.6.008 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-13 | 8.55.6.009 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  | 0
00173164/00003 | 28243981-14 | 8.55.6.010 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-15 | 8.55.6.011 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-16 | 8.55.6.012 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  | 0
00173164/00003 | 28243981 | HPVS3 - 8.55.6 | HP Stop Valve No. 3 | H |  |  |  | 205 | 140.1085 | 28722.2359
00173164/00003 | 28243981-17 | 8.55.6.013 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-18 | 8.55.6.014 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-19 | 8.55.6.015 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 60 | 140.1085 | 8406.5081 |  |  |  | 0
00173164/00003 | 28243981-20 | 8.55.6.016 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-21 | 8.55.6.017 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-22 | 8.55.6.018 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  | 0
00173164/00003 | 28243981 | HPVS4 - 8.55.6 | HP Stop Valve No. 4 | H |  |  |  | 195 | 140.1085 | 27321.1512
00173164/00003 | 28243981-23 | 8.55.6.019 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-24 | 8.55.6.020 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-25 | 8.55.6.021 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  | 0
00173164/00003 | 28243981-26 | 8.55.6.022 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-27 | 8.55.6.023 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00003 | 28243981-28 | 8.55.6.024 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  | 0
00173164/00003 | 28243981 | HPVC1 - 8.55.6 | HP Control Valve No. 1 | H |  |  |  | 205 | 140.1085 | 28722.2359
00173164/00003 | 28243981-29 | 8.55.6.025 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  | 0
00173164/00003 | 28243981-30 | 8.55.6.026 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-31 | 8.55.6.027 | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  | 0
00173164/00003 | 28243981-32 | 8.55.6.028 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-33 | 8.55.6.029 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 52 | 140.1085 | 7285.6403 |  |  |  | 0
00173164/00003 | 28243981-34 | 8.55.6.030 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00003 | 28243981-35 | 8.55.6.031 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00003 | 28243981 | HPVC2 - 8.55.6 | HP Control Valve No. 2 | H |  |  |  | 205 | 140.1085 | 28722.2359
00173164/00003 | 28243981-36 | 8.55.6.032 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  | 0
00173164/00003 | 28243981-37 | 8.55.6.033 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-38 | 8.55.6.034 | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  | 0
00173164/00003 | 28243981-39 | 8.55.6.035 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-40 | 8.55.6.036 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 52 | 140.1085 | 7285.6403 |  |  |  | 0
00173164/00003 | 28243981-41 | 8.55.6.037 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00003 | 28243981-42 | 8.55.6.038 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00003 | 28243981 | HPVC3 - 8.55.6 | HP Control Valve No. 3 | H |  |  |  | 205 | 140.1085 | 28722.2359
00173164/00003 | 28243981-43 | 8.55.6.039 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  | 0
00173164/00003 | 28243981-44 | 8.55.6.040 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-45 | 8.55.6.041 | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  | 0
00173164/00003 | 28243981-46 | 8.55.6.042 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-47 | 8.55.6.043 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 52 | 140.1085 | 7285.6403 |  |  |  | 0
00173164/00003 | 28243981-48 | 8.55.6.044 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00003 | 28243981-49 | 8.55.6.045 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00003 | 28243981 | HPVC4 - 8.55.6 | HP Control Valve No. 4 | H |  |  |  | 205 | 140.1085 | 28722.2359
00173164/00003 | 28243981-50 | 8.55.6.046 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  | 0
00173164/00003 | 28243981-51 | 8.55.6.047 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-52 | 8.55.6.048 | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  | 0
00173164/00003 | 28243981-53 | 8.55.6.049 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00003 | 28243981-54 | 8.55.6.050 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 52 | 140.1085 | 7285.6403 |  |  |  | 0
00173164/00003 | 28243981-55 | 8.55.6.051 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00003 | 28243981-56 | 8.55.6.052 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985 | MOP - 8.56.6 | Main Oil Pump (Refer to 7.6.1 in Scope of Works) | H |  |  |  | 24 | 140.1085 | 3362.6032
00173164/00001 | 28243985-02 | 8.55.6.300 | Inspect MOP pump coupling for wear. | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243985-03 | 8.55.6.301 | Record insitue measurements of pump shaft run out, | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243985-04 | 8.55.6.302 | Check end float of pump thrust bearing. | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243985-05 | 8.55.6.303 | Off site machining of thrust bearing | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  | 0
00173164/00001 | 28243985-06 | 8.55.6.304 | Measure and record run out of extension shaft and eccentricity disc. Check tightness of the bolting of the extension shaft. | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243985-07 | 8.55.6.305 | Replace with new complete pump if required | F | Contractor |  | Replace Main oil pump if required | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243985-08 | 8.55.6.306 | Modify the thrust bearing to new design "machine oil lead chamfer" if not already done. | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  | 0
00173164/00001 | 28243985-09 | 8.55.6.307 | MOP coupling alignment | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  | 0
00173164/00001 | 28243986 | OIL - 8.56.6 | Oil Labyrinths (1 - 4) | H |  |  |  | 40 | 140.1085 | 5604.3387
00173164/00001 | 28243986-27 | 8.55.6.174 | Replace the brass sealing strips in the turbine bearing oil wipers where required | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243985 | TSUX - 8.56.6 | Turbine Auxiliary Oil Pumps (Two off AC and One DC Pumps) | H |  |  |  | 13 | 140.1085 | 1821.4101
00173164/00001 | 28243985-10 | 8.55.6.308 | Remove motors and handover to Principal | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243985-11 | 8.55.6.309 | Check pump couplings, inspect pump endfloat condition | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243985-46 | 8.55.6.310 | Reinstall motors and align to pump | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243985 | TSBG - 8.56.6 | Turning Gear/ Barring Gear | H |  |  |  | 36 | 140.1085 | 5043.9048
00173164/00001 | 28243985-47 | 8.55.6.311 | Check seal clearance prior to removal. | F | Contractor |  | In 2026 Overhaul | 2 | 140.1085 | 280.2169 |  |  |  | 0
00173164/00001 | 28243986-57 | 8.55.6.312 | Remove and inspect barring mechanism. (new design barring mechanism in place) | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243985-48 | 8.55.6.126 | Align and install barring mechanism. | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243985-49 | 8.55.6.175 | The Contractor to verify manual and automatic operation at the completion of Turbine assembly | F | Contractor |  | In 2026 Overhaul | 2 | 140.1085 | 280.2169 |  |  |  | 0
00173164/00001 | 28243986-59 | 8.55.6.176 | Inspect turning gear valve internals, remove actuator and hand over to Principal, repair if necessary after blueing valve seats.. | F | Contractor |  | In 2026 Overhaul | 24 | 140.1085 | 3362.6032 |  |  |  | 0
00173164/00001 | 28243985 | ESV - 8.56.6 | Overhaul Emergency Shut Off Valve | H |  |  |  | 44.5 | 140.1085 | 6234.8268
00173164/00001 | 28243985-41 | 8.55.6.128 | Remove and replace emergency shut off valve | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243985-42 | 8.55.6.129 | Clean, inspect, overahul and blue check emergency shut off valve | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00001 | 28243985-43 | 8.55.6.130 | Repair seat if damaged | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243985-54 | TOV - 8.56.6 | Overhaul Turning Oil Valve | H |  |  |  | 37 | 140.1085 | 5184.0133
00173164/00001 | 28243985-54 | 8.55.6.131 | Remove inspect and replace turning oil valve | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243985-51 | 8.55.6.132 | Clean, inspect, blue check turning oil valve | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  | 0
00173164/00001 | 28243985-53 | 8.55.6.133 | Repair seat if damaged | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  | 0
00173164/00001 | 28243985 | GSDV - 8.56.6 | Gland Steam Dump Valve | H |  |  |  | 58 | 140.1085 | 8126.2911
00173164/00001 | 28243985-56 | 8.55.6.134 | Remove actuator | F | Contractor |  | In 2026 Overhaul | 6 | 140.1085 | 840.6508 |  |  |  | 0
00173164/00001 | 28243985-57 | 8.55.6.135 | Strip and inspect valve and carry out any repairs | F | Contractor |  | In 2026 Overhaul | 21 | 140.1085 | 2942.2778 |  |  |  | 0
00173164/00001 | 28243985-58 | 8.55.6.136 | Assembly Valve and actutor | F | Contractor |  | In 2026 Overhaul | 31 | 140.1085 | 4343.3625 |  |  |  | 0
00173164/00001 | 28243985 | GSCV - 8.56.6 | Gland Steam Control Valve | H |  |  |  | 61 | 140.1085 | 8546.6165
00173164/00001 | 28243985-59 | 8.55.6.137 | Remove actuator | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243985-60 | 8.55.6.138 | Strip and inspect valve and carry out any repairs | F | Contractor |  | In 2026 Overhaul | 21 | 140.1085 | 2942.2778 |  |  |  | 0
00173164/00001 | 28243985-61 | 8.55.6.139 | Assembly Valve and actutor | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00001 | 28243985 | BSEA - 8.56.6 | Bled Steam Extraction Actutors -S91, S86, S78 , S81. | H |  |  |  | 57 | 140.1085 | 7986.1827
00173164/00001 | 28243985-63 | 8.55.6.140 | Disassemble Actutors | F | Contractor |  | In 2026 Overhaul | 42 | 140.1085 | 5884.5556 |  |  |  | 0
00173164/00001 | 28243986-60 | 8.55.6.141 | Replace internal and external o-rings and Shaft seal | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243985-65 | 8.55.6.142 | Reassemble actuator | F | Contractor |  | In 2026 Overhaul, Commisioning Engineer to test operation of bled steam actuators. | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243985 | GOV - 8.55.6 | Governing System (Hydraulic system refurbishment) | H |  |  |  | 210 | 140.1085 | 29422.7782
00173164/00001 | 28243985-67 | 8.55.6.143 | Clean control oil inlet filters | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243985-69 | 8.55.6.144 | Inspect low vacuum trip device (replace diaphram) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-70 | 8.55.6.145 | Check starting device followup pistons (do these require spares?) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-71 | 8.55.6.146 | Over speed trip device, | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-72 | 8.55.6.147 | Electro-hydraulic convertor (EHC) Relpace spool and Bush | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-73 | 8.55.6.148 | Solenoid valves , 9 off | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-74 | 8.55.6.149 | Starting and load limit device (starting device) | F | NRG/Contractor |  | NRG Electricians Overhaul the electric motor |  |  | 0 |  |  |  | 0
00173164/00001 | 28243985-75 | 8.55.6.150 | Hydraulic speed governor (speeder gear) | F | NRG/Contractor |  | NRG Electricians Overhaul the electric motor |  |  | 0 |  |  |  | 0
00173164/00001 | 28243985-76 | 8.55.6.151 | Thrust bearing trip (at no 2 bearing) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-77 | 8.55.6.152 | Over speed trip mechanisms, 2 off on turbine shaft | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-78 | 8.55.6.153 | Follow up piston assembliesCheck integrity of HP and IP followup pistons (for control valving) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-79 | 8.55.6.154 | Overspeed Micro switches | F | NRG/Contractor |  | NRG Electricians check the switches |  |  | 0 |  |  |  | 0
00173164/00001 | 28243985-80 | 8.55.6.155 | Clean & inspect over-speed bolts & trip mechanism | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-64 | 8.55.6.156 | Bled steam actuators S91, S86, S78, S81 replace seals and o-rings | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985 | GOVC - 8.55.6 | Contractor Commissioning Engineer for Governor setup setup | H |  |  |  | 0 | 140.1085 | 0
00173164/00001 | 28243985-99 | 8.55.6.157 | Setup Main Turbine and Governor to correct OEM specification (check set up of control valve actuators, bled steam actuators), this standard and specification will be discussed with the Turbine Superintendent before work commences. | V | Contractor |  | Setup control oil/governor system as soon as possible (while Contractor fitters are available for any changes to control actuators) | 0 |  | 0 |  |  |  | 0
00173164/00001 | 28243985 | JOS - 8.55.6 | Jacking Oil System (Refer to 7.6.5 in Scope of Works) | H |  |  |  | 155 | 140.1085 | 21716.8125
00173164/00001 | 28243985-81 | 8.55.6.159 | Remove clamps and inspect jacking oil pipework / manifold for rubbing and cracks. (this scope is to be an ITP and signed off before leaving site) | F | SubContractor |  | In 2026 Overhaul | 70 | 140.1085 | 9807.5927 |  |  |  | 0
00173164/00001 | 28243985-82 | 8.55.6.160 | Replace small bore pipework with new (sub Contractor to work in with Contractor schedule) | F | SubContractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00001 | 28243985-83 | 8.55.6.161 | Strip and inspect manifold by-pass valve. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-84 | 8.55.6.162 | Replace jacking oil hoses on all (7) bearings. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243985-86 | 8.55.6.163 | IInstall new Jacking oil manifold supplied by the customer. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-87 | 8.55.6.164 | Clean and replace jacking oil magnetic oil filter. | F | Contractor |  | In 2026 Overhaul | 35 | 140.1085 | 4903.7964 |  |  |  | 0
00173164/00001 | 28243985 | MOT - 8.55.6 | Main Oil Tank and Piping (Refer to 7.6.6 in Scope of Works) | H |  |  |  | 247 | 140.1085 | 34606.7915
00173164/00001 | 28243985-88 | 8.55.6.165 | Remove and inspect vapour extraction fan internals and piping | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-89 | 8.55.6.166 | Visualy Inspect all inlet and oil take off pipes at tank for any leaks | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  | 0
00173164/00001 | 28243985-90 | 8.55.6.168 | Drain main oil tank of oil into tankers supplied by NRG. Empty date to be supplied by Contractor | F | Contractor |  | In 2026 Overhaul | 35 | 140.1085 | 4903.7964 |  |  |  | 0
00173164/00001 | 28243985-92 | 8.55.6.169 | Clean main oil tank (NRG to inspect after clean) | F | Contractor |  | In 2026 Overhaul | 74 | 140.1085 | 10368.0266 |  |  |  | 0
00173164/00001 | 28243985-93 | 8.55.6.313 | Remove and inspect main drain valve at main oil tank before oil goes back in. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243986-61 | 8.55.6.170 | Only if replacing oil, Refill main tank with new supplied turbine oil (fill date to be negoiated to match Contractor schedule) | F | Contractor |  | New oil being supplied, Contractor to remove oil and fill tank with new. | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243985-94 | 8.55.6.171 | Refill main oil tank with oil | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28244079-08 | 8.55.6.172 | Install manufactured oil strainers for filtering turbine oil system during commissioning | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243985-95 | 8.55.6.314 | Overhaul turbine thrust oil assembly, replace change over valve orings. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243985-96 | 8.55.6.173 | Contractor to set up stream liner for filtering oil for a minimun of 10 days before oil curciut is put into service | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00004 | 28243978 | EXC - 8.56.6 | Exciter Dismantling | H | Contractor |  | In 2026 Overhaul | 141 | 140.1085 | 19755.294 |  |  |  | 0
00173164/00004 | 28243978-01 | 8.56.6.001 | Remove exciter rotor, pilot exciter, coolers, bearing base, etc | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  | 0
00173164/00004 | 28243978-03 | 8.56.6.002 | Hand over the Exciter rotor to Contractor | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
|  | 8.56.6.003 | Inspection & Testing | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243978-04 | 8.56.6.004 | Clean and pressure test air coolers | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00004 | 28243978-05 | 8.56.6.005 | Inspect and test coupling bolts, etc | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00004 | 28243978-06 | 8.56.6.006 | Overhaul excitor rotor and stator | F | NRG Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243978-17 | 8.56.6.007 | Replace exciter rotor, Stator, pilot exciter, coolers, bearing base to correct specifications | F | Contractor |  | In 2026 Overhaul | 41 | 140.1085 | 5744.4472 |  |  |  | 0
00173164/00004 | 28243979 | GEND - 8.56.6 | Generator Minor Overhaul in 2026 only. | H |  |  |  | 361 | 140.1085 | 50579.1569
|  | 8.56.6.008 | Dismantling | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-47 | 8.56.6.009 | Prepare the Generator and Stator for robotic inspection performed by Contractor. | F | Contractor |  | In 2026 Overhaul (Robotic inspection required for Minor Gen Overhaul) | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00004 | 28243986-62 | 8.56.6.010 | Remove Number 4 Bearing Pedestal Cover | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  | 0
00173164/00004 | 28243979-02 | 8.56.6.011 | Remove bearings 5 & 6 outer oil wipers and top support covers | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  | 0
00173164/00004 | 28243986-63 | 8.56.6.012 | Remove No 4 bearing bridge and top half bearing | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  | 0
00173164/00004 | 28243979-04 | 8.56.6.013 | Perform strip down measurements of bearings 5 & 6 & unbolt upper bearings | F | Contractor |  | In 2026 Overhaul | 45 | 140.1085 | 6304.881 |  |  |  | 0
00173164/00004 | 28243979-05 | 8.56.6.014 | Remove upper and lower bearings 5 & 6 | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  | 0
00173164/00004 | 28243986-67 | 8.56.6.015 | Perform Bearing 4 Stripdown Measurements (Top lead check etc) | F | Contractor |  | In 2026 Overhaul | 42 | 140.1085 | 5884.5556 |  |  |  | 0
00173164/00004 | 28243979-07 | 8.56.6.016 | Undo LP-Gen Coupling and perform Coupling Alignment | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00004 | 28243979-08 | 8.56.6.017 | Remove outer oil wipers and top support frame | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  | 0
00173164/00004 | 28243979-09 | 8.56.6.018 | Remove H2 seal ring holders | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00004 | 28243979-10 | 8.56.6.019 | Remove bolts from inner labyrinths (EE) (EEnd only as we are only removing the top end shield for robot access) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  | 0
00173164/00004 | 28243979-11 | 8.56.6.020 | Reinstall bearings 5 & 6 (lower halves) | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  | 0
00173164/00004 | 28243979-12 | 8.56.6.021 | Remove EE upper end shield only(Rescue squad required) | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00004 | 28243979-13 | 8.56.6.022 | Support rotor at EE (Install bracket and sling) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  | 0
00173164/00004 | 28243979-14 | 8.56.6.023 | Remove bearing 6 | F | Contractor |  | In 2026 Overhaul | 14 | 140.1085 | 1961.5185 |  |  |  | 0
00173164/00004 | 28243979-01 | 8.56.6.024 | Unbolt and lower EE end shield (Floor removal policy to be in place) | F | Contractor |  | Check to see if this is required for robotic inspection (Contractor to determine scope) |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-15 | 8.56.6.026 | Remove bearing 5 | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  | 0
00173164/00004 | 28243979 | GENI - 8.56.6 | Inspection & Repairs | H |  |  |  | 207 | 140.1085 | 29002.4528
|  | 8.56.6.030 | Generator H2 Seals (Inspection & Repairs) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-17 | 8.56.6.031 | Clean H2 seal ring holders and measure (supply size to NRG) | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00004 | 28243979-18 | 8.56.6.032 | Rectify H2 Seal Holder (NRG) | F | Contractor |  | In 2026 Overhaul | 7 | 140.1085 | 980.7593 |  |  |  | 0
00173164/00004 | 28243979-19 | 8.56.6.033 | Machine new H2 seals | F | NRG |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-20 | 8.56.6.034 | Measure new seal rings and check fittment | F | Contractor |  | In 2026 Overhaul | 26 | 140.1085 | 3642.8202 |  |  |  | 0
00173164/00004 | 28243979-21 | 8.56.6.035 | Replace inner labyrinths seal strips if required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00004 | 28243979-22 | 8.56.6.036 | Machine inner labyrinths (only inspecting EE inner labyrinth) | F | NRG |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-23 | 8.56.6.037 | Prepare new insulation package (Holes have to be drilled in OEM supplied gaskets) | F | Contractor |  | In 2026 Overhaul | 104 | 140.1085 | 14571.2806 |  |  |  | 0
00173164/00004 | 28243979 | GENR - 8.56.6 | Generator Rotor Inspection and testing of H2 up shaft lead seals. | H |  |  |  | 10 | 140.1085 | 1401.0847
00173164/00004 | 28243979-03 | 8.56.6.038 | When the Exciter shaft is removed, Contractor to perform air leak test on Generator shaft with pressure plare (report findings toNRG Engineering) | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00004 | 28243979 | GENE - 8.56.6 | Generator End Shields | H |  |  |  | 80 | 140.1085 | 11208.6774
00173164/00004 | 28243979-24 | 8.56.6.048 | Clean end shields & check mating surfaces (only perform this operation at EE) | F | Contractor |  | Clean for reinstallation of top end shield | 80 | 140.1085 | 11208.6774 |  |  |  | 0
00173164/00004 | 28243979-25 | 8.56.6.049 | Blue Checking of Bottom Sphericals on Bearing's 5 & 6 | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979 | GENRR - 8.56.6 | Robotic Inspection being performed on Stator and Rotor (Contractor to determine which tests are being performed by the Robot) | H |  |  | In 2026 Overhaul | 0 | 140.1085 | 0
00173164/00004 | 28243979-26 | 8.56.6.053 | Stator Fact Finding Visual Inspection | F | NRG |  | NRG Engineering |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-27 | 8.56.6.054 | Stator inspection performed by Contractor engineering (Contractor to define scope being performed with Robot) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979 | GENW - 8.56.6 | Resin End Winding Treatment | H |  |  |  | 0 | 140.1085 | 0
00173164/00004 | 28243979-28 | 8.56.6.055 | Preparation | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-29 | 8.56.6.056 | Cleaning Endwinding & Mask areas | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-30 | 8.56.6.057 | Heating | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-31 | 8.56.6.058 | Treat overhang with Resin | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-32 | 8.56.6.059 | Finalise Works | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979 | GENRP - 8.56.6 | Robotic Inspection being performed on Stator and Rotor (Contractor to determine which tests are being performed by the Robot) | H |  |  |  | 0 | 140.1085 | 0
00173164/00004 | 28243979-34 | 8.56.6.060 | 1.Winding Resistance measurement – stator | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-35 | 8.56.6.061 | 2.Insulation Test & Polarization Index - stator | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-36 | 8.56.6.062 | 3.DC Controlled Over-voltage Tests - stator | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-37 | 8.56.6.063 | 4.Dielectric Dissipation Factor and Capacitance testing - stator | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-38 | 8.56.6.064 | 5.Partial Discharge testing of the stator winding (Test gear should be capable of carring out PD on phases at the same time) | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-39 | 8.56.6.065 | 6.RSO testing - rotor | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-40 | 8.56.6.066 | 7.Insulation Resistance – rotor | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-41 | 8.56.6.067 | 8.Winding Resistance – rotor | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-42 | 8.56.6.070 | 11.RTDs Test – (Resistance Test & Insulation Test) | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-43 | 8.56.6.071 | 12.Rotor Inspection | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-44 | 8.56.6.072 | 13.Stator Inspection | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-45 | 8.56.6.073 | 14.Slot Wedge Deflection Test | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979-46 | 8.56.6.074 | 15.Bump Test (Stator end windings) | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 |  | 8.56.6.075 | 16.Robotic inspection of Stator and rotor | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00004 | 28243979 | GENRA - 8.56.6 | Reassembly / Generator and Exciter | H |  |  |  | 340 | 140.1085 | 47636.879
00173164/00004 | 28243979-06 | 8.56.6.076 | Remove the clean condition tents & store | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  | 0
00173164/00004 | 28243979-48 | 8.56.6.086 | Insert bearings 5 & 6 (lower halves) | F | Contractor |  | In 2026 Overhaul | 14 | 140.1085 | 1961.5185 |  |  |  | 0
00173164/00004 | 28243979-49 | 8.56.6.087 | Install air gap seal (Exciter End) | F | Contractor |  | In 2026 Overhaul | 24 | 140.1085 | 3362.6032 |  |  |  | 0
00173164/00004 | 28243979-50 | 8.56.6.088 | Install upper Ends Shield Exciter End (Rescue Squad) | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00004 | 28243979-51 | 8.56.6.092 | Install inner labyrinths (EE only as other end is not being disassembled) | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00004 | 28243979-52 | 8.56.6.093 | Seal Oil Flush | F | Contractor |  | In 2026 Overhaul | 32 | 140.1085 | 4483.471 |  |  |  | 0
00173164/00004 | 28243979-53 | 8.56.6.094 | Complete tightening of inner labyrinths | F | Contractor |  | EEnd only | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00004 | 28243979-54 | 8.56.6.095 | Pump sealant through end shields | F | Contractor |  | EEnd only | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00004 | 28243979-55 | 8.56.6.096 | Remove bearings 5 & 6 | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  | 0
00173164/00004 | 28243979-56 | 8.56.6.097 | Install H2 Seal (First Set) | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00004 | 28243979-57 | 8.56.6.098 | Install H2 Seal (Second Set) | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00004 | 28243979-58 | 8.56.6.101 | Complete bearing cover preliminary installation (For megger check) | F | Contractor |  | In 2026 Overhaul | 38 | 140.1085 | 5324.1218 |  |  |  | 0
00173164/00004 | 28243979-59 | 8.56.6.102 | Air pressure test to OEM specifications | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243986 | BEA - 8.56.6 | Bearings (5,6 & 7) | H |  |  |  | 115 | 140.1085 | 16112.4738
00173164/00001 | 28243986-23 | 8.56.6.103 | Clean, inspect and carry out measurement survey on bearings | F | Contractor |  | In 2026 Overhaul | 75 | 140.1085 | 10508.1351 |  |  |  | 0
00173164/00001 |  | 8.56.6.104 | NDT Bearing's 5,6 & 7 | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00001 | 28243986-24 | 8.56.6.105 | Clean bearings after NDT testing | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243986 | OL - 8.56.6 | Oil Labyrinths (5,6 & 7) | H | Contractor |  |  | 75 | 140.1085 | 10508.1351
00173164/00001 | 28243986-25 | 8.56.6.106 | Replace brass sealing strips where required | F | Contractor |  | In 2026 Overhaul | 75 | 140.1085 | 10508.1351 |  |  |  | 0
00173164/00001 |  | 8.56.6.107 | Machine oil labyrinths | F | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00001 | 28243982 | H2S - 8.56.6 | H2 Seal Oil System | H |  |  |  | 397.5 | 140.1085 | 55693.1159
00173164/00001 | 28243982-17 | 8.56.6.108 | Inspect AC and DC oil pump non return valves. | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243982-18 | 8.56.6.109 | Remove AC / DC pump motors, for electricians to Overhaul | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243982-19 | 8.56.6.110 | Remove and replace AC and DC seal oil pumps with refurbished pumps. | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  | 0
00173164/00001 | 28243982-46 | 8.56.6.111 | Replace and align AC and DC Overhauled electric motors | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243982-20 | 8.56.6.112 | Clean all strainers on seal oil system. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243982-21 | 8.56.6.113 | Inspect and clean main and intermediate seal oil tanks. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243982-22 | 8.56.6.114 | Inspect main seal oil float valve and seat. | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  | 0
00173164/00001 | 28243982-23 | 8.56.6.115 | Inspect intermediate seal oil float valve and seat. | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  | 0
00173164/00001 | 28243982-24 | 8.56.6.116 | Inspect and repair hydrogen drier isolation valves. – ST13-S501 and ST13-S507 | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  | 0
00173164/00001 | 28243982-25 | 8.56.6.117 | Inspect and repair hydrogen valves – ST11-S501, ST11-S502, ST11-S516, ST11-S517, ST11-S520, ST11-S521 and ST11-S525.S589 | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243982-26 | 8.56.6.118 | Inspect and repair seal oil valves – SU11-S596, SU11-S597, SU11-598, SU11-S599, SU14 – S510, SU14– S511, SU14 – S512, SU14 – S513, SU14 – S514, SU14 – S515. | F | Contractor |  | In 2026 Overhaul | 43 | 140.1085 | 6024.6641 |  |  |  | 0
00173164/00001 | 28243982-27 | 8.56.6.119 | Inspect and repair hydrogen valves – ST12-S522, S521, S529. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243982-28 | 8.56.6.120 | Inspect and repair CO2 relief valves, (hi and low pressure, replace with new) | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243982-29 | 8.56.6.121 | Inspect and replace diaphragm on H2 analyzer regulator (large and small reg) Please measure for future diaphram sizing, report sizing to NRG Engineering | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243982-30 | 8.56.6.122 | Inspect and replace diaphrams in H2 fill station pressure reducer valves- 3 off (ST12- N523, N524, N531). Please measure for future diaphram sizing, report sizes of diaphram to NRG Engineering. | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243982-31 | 8.56.6.123 | Replace all seal oil pipework gaskets. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243982-32 | 8.56.6.124 | Inspect generator liquid detection sight glass and replace gaskets. | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  | 0
00173164/00001 | 28243982-33 | 8.56.6.125 | Inspect liquid level detection valves SP11-533, SP11-531, SP11-532, SP11-539, SP11-501, SP11-534 | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243982-34 | 8.56.6.126 | Inspect and replace seal oil cooler top “O” rings. Pressure test seal oil coolers to specification. | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  | 0
00173164/00001 | 28243982-35 | 8.56.6.127 | Inspect, flush and clean all hydrogen vent pipework. | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243982-36 | 8.56.6.128 | Visually inspect all hydrogen pipework, manifold and clamps to check for wear or leaks. | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243982-37 | 8.56.6.129 | Inspect, flush and clean bearing vapour extraction fan (AVR floor). | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243982-38 | 8.56.6.130 | Replace all valves locking spacers and fixing chains. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243982-39 | 8.56.6.131 | Change out A and B valves with Overhauled valves provided from NRG store | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28244079-07 | 8.56.6.132 | Commission A and B valves to correct pressure settings. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243982 | HSOP - 8.56.6 | Hydrogen Seal Oil Plant – After Oil Flush | H |  |  |  | 23.5 | 140.1085 | 3292.549
00173164/00001 | 28243982-49 | 8.56.6.133 | Inspect main seal oil float valve and seat (have NRG Turbine inspector inspect seat) | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243982-50 | 8.56.6.134 | Inspect intermediate seal oil float valve and seat for debris(have NRG turbine inspector inspect seat) | F | Contractor |  | In 2026 Overhaul | 13 | 140.1085 | 1821.4101 |  |  |  | 0
00173164/00001 | 28243986 | TBCD - 8.55.6 | Turbine Bearings & Couplings Disassembly | H |  |  |  | 304 | 140.1085 | 42592.9742
00173164/00001 |  | 8.55.6.180 | Disconnect and remove the instrumentation from the turbine bearings pedestals |  | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00001 | 28243986-04 | 8.55.6.181 | Remove the bearing pedestal covers from bearings 1, 2, 3 & 4 including oil labyrinths | F | Contractor |  | In 2026 Overhaul | 110 | 140.1085 | 15411.9315 |  |  |  | 0
00173164/00001 |  | 8.55.6.182 | Disconnect and remove the internal instrumentation from the bearings |  | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00001 | 28243986-06 | 8.55.6.183 | Measure the thrust bearing axial clearance | F | Contractor |  | In 2026 Overhaul | 16 | 140.1085 | 2241.7355 |  |  |  | 0
00173164/00001 | 28243986-08 | 8.55.6.184 | Remove the bearing bridges and top halves of bearings 1, 2, 3 & 4 | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243986-07 | 8.55.6.185 | Record axial & radial positions of the turbine rotors to the turbine casings and bearing pedestals prior to bearing removal | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243986-11 | 8.55.6.186 | Measure and record HP & IP casing to rotor roll out check | O | Contractor |  | Only if required | 24 | 140.1085 | 3362.6032 |  |  |  | 0
00173164/00001 | 28243986-10 | 8.55.6.187 | Remove lower thrust bearing and remove thrust pads | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243986-13 | 8.55.6.188 | Install thrust bearing and perform axial clearance checks on HP/IP rotors coupled | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243986-12 | 8.55.6.189 | Reinstall with 2 thrust pads fitted | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  | 0
00173164/00001 | 28243986-14 | 8.55.6.191 | Perform Stub Shaft Runout | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  | 0
00173164/00001 | 28243986-15 | 8.55.6.192 | Remove windage plates from all couplings | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  | 0
00173164/00001 | 28243986 | TBCI - 8.55.6 | Inspection | H |  |  |  | 85 | 140.1085 | 11909.2198
00173164/00001 | 28243986-18 | 8.55.6.195 | Remove all lower turbine bearings for visual inspection on disessembly | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 |  | 8.55.6.196 | NDT all bearings and thrust pads | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00001 | 28243986-19 | 8.55.6.197 | Clean, visually inspect and measure the bearing clearances of bearings by lead check only on dissemessbly (1 - 4 bearings) and thrust pads | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243986-65 | 8.55.6.198 | Replace the brass sealing strips on oil wipers only as required | V | Contractor | allow for 6 off oil wipers | In 2026 Overhaul | 65 | 140.1085 | 9107.0504 |  |  |  | 0
00173164/00001 |  | 8.55.6.199 | Machine oil labyrinths to nominated sizes as required |  | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00001 | 28243985 | ABG - 8.55.6 | Automatic barring gear (if not already fitted) | H |  |  |  | 38 | 140.1085 | 5324.1218
00173164/00001 | 28243985-38 | 8.55.6.200 | Remove and inspect mechanical barring mechanism | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  | 0
00173164/00001 | 28243985-91 | 8.55.6.201 | Contractor Test fit new modifided barring gear | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243986-58 | 8.55.6.202 | Install new automatic barring gear when no.3 bearing lid is on for final time. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243986 | BPFB - 8.55.6 | Bearing pedestal Foundation bolt hydraulic tensioning, Assembly | H |  |  |  | 358.5 | 140.1085 | 50228.8857
00173164/00001 | 28243986-29 | 8.55.6.101 | Install all the lower turbine bearings and connect lift oil hoses | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  | 0
00173164/00001 | 28243986-33 | 8.55.6.102 | Tighten all couplings and perform concentricity checks | F | Contractor |  | In 2026 Overhaul | 45 | 140.1085 | 6304.881 |  |  |  | 0
00173164/00001 | 28243986-34 | 8.55.6.103 | Measure and record all the bearing pedestal radial and axial references (on completion of casing rollouts | F | Contractor |  | In 2026 Overhaul | 35 | 140.1085 | 4903.7964 |  |  |  | 0
00173164/00001 | 28243986-35 | 8.55.6.104 | Install and set the oil wipers | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243986-42 | 8.55.6.105 | Assemble the bearings covers for oil flushing | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243986-43 | 8.55.6.106 | Perform oil flushing with strainers on flushing pipes | F | Contractor |  | Utilize best method of oil flushing for Unit 2 in 2026 | 60 | 140.1085 | 8406.5081 |  |  |  | 0
00173164/00001 | 28243986-44 | 8.55.6.107 | Final assembly of turbine bearings & bearing bridges including clearance checks | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  | 0
00173164/00001 |  | 8.55.6.108 | Set up the differential expansion devices and internal instrumentation | F | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00001 | 28243986-46 | 8.55.6.109 | Final assembly of the bearing pedestals | F | Contractor |  | In 2026 Overhaul | 63.5 | 140.1085 | 8896.8877 |  |  |  | 0
00173164/00001 |  | 8.55.6.110 | Refit the external instrumentation | F | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00001 | 28243986 | FCA - 8.55.6 | Final Coupling Alignments & Bearing Closure | H |  |  |  | 370 | 140.1085 | 51840.1331
00173164/00001 |  | 8.55.6.111 | Pressurise Generator for LP- Gen Coupling alignment- 100Kpa-350Kpa | F | NRG/Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00001 | 28243986-37 | 8.55.6.112 | Complete bearing cover preliminary installation (For megger check) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  | 0
00173164/00001 | 28243986-38 | 8.55.6.113 | Perform coupling alignment readings of LP to Generator Rotor | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243986-39 | 8.55.6.114 | Adjust stator to correct alignment | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243986-66 | 8.55.6.115 | Prepare bearings for oil flushing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243979-68 | 8.55.6.116 | Oil flush seal oil system | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243978-20 | 8.55.6.117 | Reinstall exciter Rotor | F | Contractor |  | In 2026 Overhaul | 80 | 140.1085 | 11208.6774 |  |  |  | 0
00173164/00001 | 28243986-40 | 8.55.6.118 | Perform Gen-Exc Coupling Alignment, tighten coupling bolts and perform concentricity check, install windage plates. | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 | 28243986-41 | 8.55.6.119 | Air pressure test (24 hour pressure test) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 |  | 8.55.6.120 | Differential expansion set up (NRG) | F | NRG/Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00001 | 28243986-54 | 8.55.6.121 | Fully assemble bearings & covers | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
00173164/00001 |  | 8.55.6.122 | Refit external instrumentation | F | NRG/Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  | 0
00173164/00001 | 28243986-55 | 8.55.6.123 | Prepare No. 5 and 6 bearings for oil flushing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  | 0
00173164/00001 | 28243986-56 | 8.55.6.124 | Prepare No.7 bearing for oil flushing | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  | 0
00173164/00001 | 28243978-18 | 8.55.6.125 | Install, pilot exciter, coolers, etc. | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  | 0
General
[7 empty] | TOTAL hrs | 5952 | 140.1085 | 833925.6 |  | 0 | #DIV/0! | 0 | 0 | [24 empty] | 0 | 0 | 0 |  |  |  | 0
Note on J150: Mustapha, Isa: SEAG