## Total TCE
Siemens Energy Pty Ltd - Rev3 - 19/02/2026 | Target Cost Estimate |  |  | Adjusted Target Cost Estimate |  |  | Contract Execution
Activity description | Estimated Hours | Gang Rate | Estimated Cost | Estimated Hours | Gang Rate | Estimated Cost | Actual Hours to date | Actual Gang Rate | Actual Cost to date | Forecast | Percentage of Hours Complete | Percentage of Cost Complete
Overheads |  |  | 3017845.6 | 0 | #DIV/0! | 0 | 0 |  | 0 | 0
Skilled Labour | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total included in KPI |  |  | #REF! |  |  | #REF! |  |  | #REF! | #REF!
Overheads (Not included in KPI) | 8714.5 | 331.0122 | 2884605.6 | 0 | #DIV/0! | 0 | 0 | N/A | 0 | 0
Target Cost Estimate (excl.GST) |  |  | #REF! |  |  | #REF! |  |  | #REF! | #REF!
[8 empty] | Variations | 0 | 0
Incentive
[8 empty] | Total Contract Spend | #REF! | #REF!
Notes
Variations for additional work are to be mutually agreed and charged at Schedule of Rates or a fixed price.
The TCE is to be adjusted for work scope that is removed or reduced and reflected in 'Adjusted Target Cost Estimate'.
Total Contract Spend' should be equavalent to 'Total' on Invoice Summary tab.
Overheads are to be a capped estimate.

## Overheads
Scope of Work |  |  |  |  | Target Cost Estimate |  |  |  | Adjusted - Target Cost Estimate |  |  |  | Contract Execution
Work Order | Service Order Number/Release | Item ID | Activity description | Overhead Labour - Included in KPI | Hours or Units | Type of Unit (per Hour, Day, Week, flight, Tonne etc). | Gang rate or Unit Rate | Total Cost | Hours or Units | Type of Unit (per Hour, Day, Week, flight, Tonne etc). | Gang rate or Unit Rate | Total Cost | Week 1 - Actual Hours | Week 1 - Actual Total Cost (Including Overhead and Profit) | Week 2 - Actual Hours | Week 2 - Actual Total Cost (Including Overhead and Profit) | Week 3 - Actual Hours | Week 3 - Actual Total Cost (Including Overhead and Profit) | Week 4 - Actual Hours | Week 4 - Actual Total Cost (Including Overhead and Profit) | Week 5 - Actual Hours | Week 5 - Actual Total Cost (Including Overhead and Profit) | Week 6 - Actual Hours | Week 6 - Actual Total Cost (Including Overhead and Profit) | Week 7 - Actual Hours | Week 7 - Actual Total Cost (Including Overhead and Profit) | Week 8 - Actual Hours | Week 8 - Actual Total Cost (Including Overhead and Profit) | Week 9 - Actual Hours | Week 9 - Actual Total Cost (Including Overhead and Profit) | Week 10 - Actual Hours | Week 10 - Actual Total Cost (Including Overhead and Profit) | Week 11 - Actual Hours | Week 11 - Actual Total Cost (Including Overhead and Profit) | Variation Hours | Variation Amount | Total - Actual Hours | Total - Actual Total Cost | Actual Gang Rate | Percentage of Hours or Units Complete | Percentage of Cost Used | Task Complete | Forecast Cost for Completion of Project
|  | 2.02.1 | Pre Outage Planning and Management
| 00173164/00002 | 2.02.1.1 | Project Manager | No | 100 | fixed hours | 315 | 31500 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.1.2 | Plant Supervisors | No | 60 | fixed hours | 300 | 18000 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.1.3 | Quality Officers / Project Engineer | No | 100 | fixed hours | 236 | 23600 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.1.4 | Bank Guarantee | No | 1 | fixed price | 4720 | 4720 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.1.5 | Levy (Portable Long Service Leave Scheme) | No | 1 | fixed price | 31300 | 31300 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
|  | 2.02.1.12 |  | No |  |  |  | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
|  | 2.02.2 | Outage Duration Project Management | [5 empty] | 910209.6 | actual | [26 empty] | 0 |  | N/A | #DIV/0! | #DIV/0! |  | 0
| 00173164/00002 | 2.02.2.1 | Project Manager | No | 572 | hours | 336.0909 | 192244 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.2.2 | Supervisors dayshift | No | 1034 | hours | 320.9478 | 331860 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.2.3 | Quality Officers dayshift | No | 946 | hours | 253.0782 | 239412 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.2.4 | Site Admin | No | 539 | hours | 113.0197 | 60917.6 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.2.5 | Safety Officer | No | 539 | hours | 159.1391 | 85776 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
|  | 2.02.3 | Post Outage Management | [33 empty] | 0 |  | N/A | #DIV/0! | #DIV/0! |  | 0
| 00173164/00002 | 2.02.3.1 | Project Manager | No | 60 | fixed hours | 315 | 18900 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.3.2 | Site Supervision (Day Shift) | No | 30 | fixed hours | 300 | 9000 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.3.3 | Quality Officers / Project Engineer | No | 30 | fixed hours | 236 | 7080 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
|  | 2.02.4 | Site compliance, travel, accommodation & LAHA | [33 empty] | 0 |  | N/A | #DIV/0! | #DIV/0! |  | 0
| 00173164/00002 | 2.02.4.1 | Flights for PM team & supervision | No | 7 | cost plus | 1120 | 7840 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.4.2 | Accommodation for PM team & supervision | No | 396 | cost plus | 177 | 70092 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.4.3 | Living away from home allowance (LAHA) for PM team & supervision | No | 396 | rates | 183 | 72468 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.4.4 | Travel Time PM Team and Supervision | No | 112 | rates | 234 | 26208 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.4.5 | Accommodation for Trades Labour (incl.site establish./demob period) | No | 459 | cost plus | 177 | 81243 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.4.6 | LAHA for Trades Labour (incl.site establish./demob period) | No | 785 | rates | 141 | 110685 |  |  |  | 0
| 00173164/00002 | 2.02.4.7 | Car & Ute(1x) Hire + daily fuel - PM Team and Supervision/Overseas | No | 260 | cost plus | 76 | 19760 |  |  |  | 0
| 00173164/00002 | 2.02.4.8 | Medical costs for Overseas Personnel (assume 1 ppl) | No | 1 | cost plus | 605 | 605 |  |  |  | 0
| 00173164/00002 | 2.02.4.9 | Blue Dog / White Card Training for Overseas personnel (assume only 1 ppl + labour 8 hours) | No | 1 | cost plus | 2734 | 2734 |  |  |  | 0
| 00173164/00002 | 2.02.4.10 | Car Hire - Trades | No | 124 | cost plus | 71 | 8804 |  |  |  | 0
| 00173164/00002 | 2.02.4.11 | Induction backoffice for all personnel (4hrs x Rates) + Rapid Global fees | No | 1 | cost plus & hours | 9977 | 9977 |  |  |  | 0
| 00173164/00002 | 2.02.4.12 | Travel allowances for Trades | No | 240 | hours & rates | 30 | 7200
| 00173164/00002 | 2.02.4.13 | Travel Time Trades Labour | No | 256 | rates | 121 | 30976 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
|  | 2.02.5 | Indirect labour costs (project duration including mob/demob) | [33 empty] | 0 |  | N/A | #DIV/0! | #DIV/0! |  | 0
| 00173164/00002 | 2.02.5.1 | Site Establishment & demob (trades labour hrs only) | No | 627 | hours | 129 | 80883 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.2 | SubContractor - NDT | No | 1 | cost plus | 117648 | 117648 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.3 | SubContractor - Insulation removal and reinstall | No | 1 | cost plus | 141177 | 141177 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.4 | SubContractor - Generator Works Winders |  |  | cost plus |  | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.5 | SubContractor - Offsite (local) Machining works allowance | No | 1 | cost plus | 23530 | 23530 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.6 | SubContractor - HV Testing incl. own power supply | No | 1 | cost plus | 58824 | 58824 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.7 | SubContractor - Oil coolers freight to customer's third party workshop | No |  | cost plus | 0 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.8 | SubContractor - local road transport to workshop/grit blasting | No | 1 | cost plus | 4706 | 4706 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.9 | Crane drivers "Overheads" labour dayshifts | No | 437.5 | hours | 136 | 59500 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.10 | General/indirect labour (to be used for variations, etc.) | No |  | hours |  | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.11 | Consumables & PPE | No | 1 | cost plus | 36280 | 36280 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.5.12 | SubContractor - Offsite (local) grit blasting allowance | No | 1 | cost plus | 23530 | 23530 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
|  | 2.02.6 | Contractor owned vehicles, tooling, plant and equipment |  |  |  |  | 133240 | [28 empty] | 0 |  | N/A | #DIV/0! | #DIV/0! |  | 0
| 00173164/00002 | 2.02.6.1 | Tool Container (20ft) | No | 7 | weeks | 6056 | 42392 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.2 | Rigging Container (20ft) | No | 7 | weeks | 4658 | 32606 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.3 | Side opening workshop container – 10ft | No | 0 | weeks | 1631 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.4 | General workshop container – 20ft | No | 5 | weeks | 2329 | 11645 |  |  |  | 0
| 00173164/00002 | 2.02.6.5 | Storage container – 20ft | No | 7 | weeks | 299 | 2093 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.6 | Induction end bell heater (for Generator ret.rings) N/A | No |  | days |  | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.7 | Induction bolt heater – two units | No |  | days |  | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.8 | Generator tunnel camera (Reizler), 51mm lens | No | 15 | days | 231 | 3465 |  |  |  | 0
| 00173164/00002 | 2.02.6.9 | Hydraulic tensioning unit | No | 4 | weeks | 1294 | 5176 |  |  |  | 0
| 00173164/00002 | 2.02.6.10 | Parts washer, ultrasonic, 50 litres | No |  | weeks |  | 0 |  |  |  | 0
| 00173164/00002 | 2.02.6.11 | Bore micrometre kit | No | 4 | weeks | 1006 | 4024 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.12 | Chemical storage cabinet, flammable liquid – 80 can | No | 7 | weeks | 177 | 1239 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.13 | Transport SEA tooling containers to/from site | No | 1 | cost plus | 25890 | 25890 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.14 | Generator - Robotic Inspection (see overseas below) | No |  | weeks |  | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.15 | printer, photocopier & office stationary | No | 1 | cost plus | 4710 | 4710 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.16 | Temp.fences hire + transport | No | 0 | cost plus | 5890 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.6.17 | Forklift ~2.5t hire + transport | No | 0 | cost plus | 0 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
|  | 2.02.7 | Overseas Specialist Personnel (Mobilisation and Demobilisation & labour hours & tools hire). | [33 empty] | 0 |  | N/A | #DIV/0! | #DIV/0! |  | 0
| 00173164/00002 | 2.02.7.1 | SEAG SST hydraulic/governor Technician - site labour hours | No | 260 | hours (FOREX) | 474 | 123240 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.2 | SEAG SST hydraulic/governor Technician - mobilisation fee | No | 1 | rates (FOREX) | 21731 | 21731 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.3 | SEAG SST hydraulic/governor Technician - flights & LAHA/accom. | No | 1 | rates (FOREX) and cost plus | 27199 | 27199 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.4 | SEAG SST Commissioning Engineer - site labour hours | No | 104 | hours (FOREX) | 869 | 90376 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.5 | SEAG SST Commissioning Engineer - mobilisation fee | No | 1 | rates (FOREX) | 44850 | 44850 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.6 | SEAG SST Commissioning Engineer - flights & LAHA/accom. | No | 1 | rates (FOREX) and cost plus | 20728 | 20728 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.7 | SEAG Generator (GN) FastGen Engineer - site labour hours | No | 115 | hours (FOREX) | 840 | 96600 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.8 | SEAG GN FastGen Engineer - mobilisation fee | No | 1 | rates (FOREX) | 44850 | 44850 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.9 | SEAG GN FastGen & Fact Finder Engineer - flights & LAHA/accom. | No | 1 | rates (FOREX) and cost plus | 20728 | 20728 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.10 | Visas for SEAG ppl | No | 3 | rates | 2640 | 7920 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.11 | SEAG SST Balancing Engineer Remote hours | No | 0 | hours (FOREX) | 775 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.12 | SEAG Backoffice GN bump testing Engineering | No | 14 | hours (FOREX) | 511 | 7154 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.13 | SEAG Backoffice SST Engineering & Field Service remote support | No | 0 | hours (FOREX) | 463 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.14 | SEAG Backoffice GN Engineering & Field Service remote support | No | 0 | hours (FOREX) | 463 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.15 | SEAG SST governor & commissioning tooling tools hire 12 weeks | No | 12 | weeks (FOREX) | 2900 | 34800 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.16 | SEAG GN FastGen (Robot) tool 7 weeks hire | No | 7 | weeks (FOREX) | 14030 | 98210 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.17 | SEAG GN fact finding (rotor not out) tools 7 weeks hire | No | 7 | weeks (FOREX) | 1500 | 10500 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.18 | SEAG GN bump testing tool 6 weeks hire | No | 6 | weeks (FOREX) | 4000 | 24000 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.19 | SEAG SST Coupling Expander Tool 8 weeks hire | No | 0 | weeks (FOREX) | 400 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.20 | SEAG SST balancing tooling 7weeks hire | No | 0 | weeks (FOREX) | 4630 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.21 | Transport SEAG tools from overseas to site and return | No | 1 | cost plus | 29500 | 29500 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.23 | Option SEAG SST blading technician - site labour hours | No | 0 | hours (FOREX) | 470 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.24 | Option SEAG SST blading technician - mobilisation, flights, visa, LAHA/accom. | No | 0 | rates (FOREX) and cost plus | 50850 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
| 00173164/00002 | 2.02.7.25 | Option SEAG SST blading tools 9 weeks & consumables | No | 0 | weeks (FOREX) | 31750 | 0 |  |  |  | 0 | [24 empty] | 0 | 0 | N/A | #DIV/0! | #DIV/0! | No | 0
2.02.8
| 00173164/00002 | 2.02.8.31 | Variation V001
| 00173164/00002 | 2.02.8.32 | Variation V002
| 00173164/00002 | 2.02.8.33 | Variation V003
| 00173164/00002 | 2.02.8.34 | Variation V004
| 00173164/00002 | 2.02.8.35 | Variation V005
| 00173164/00002 | 2.02.8.36 | Variation V006
| 00173164/00002 | 2.02.8.37 | Variation V007
| 00173164/00002 | 2.02.7.38 | Variation V008
|  |  | Total |  |  |  |  | 3017845.6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | #REF! |  | 0
|  |  | Overheads - Labour |  | 0 |  | #DIV/0! | 0 | 0 |  | #DIV/0! | 0 | [24 empty] | 0 | 0 |  |  |  |  | 0
|  |  | Overheads - Non Labour excluded from the KPI |  | 8714.5 |  |  | 2884605.6 | 0 |  | #DIV/0! | 0 | [24 empty] | 0 | 0 |  |  |  |  | 0

## Skilled Labour
|  |  | Scope of Work |  |  |  |  | Target Cost Estimate (19/2/26) |  |  |  |  | Adjusted Target Cost Estimate |  |  |  | Contract Execution
00173164/00001 | 28243985-08 | 8.55.6.116 | Off site machining of thrust bearing | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  |  | 0
Turbine
HP Turbine
|  |  | HP Dismantling (Refer to 7.2.1 and 7.2.2 of Scope of Works) | [8 empty] | 5604.3387
|  |  | Removal of HP Turbine from Pedestals | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt & support the exhaust pipes | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Mark & cut gland steam pipes | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Semi unbolt the front and rear outer gland housings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-08 | 8.55.6.119 | Modify the thrust bearing to new design "machine oil lead chamfer" if not already done. | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  |  | 0
|  |  | Pack and secure/support HP valve stands | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Disconnect MS 1 inlet connections | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Disconnect MS 2 inlet connections | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Disconnect MS 3 inlet connections | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Disconnect MS 4 inlet connections | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243986-27 | 8.55.6.174 | Replace the brass sealing strips in the turbine bearing oil wipers where required | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
|  |  | Jack the HP casing forward to disengage the HP/IP coupling | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove outer casing to lay down area and support on steel frames (28) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Removal of Inner Casing, Rotor and Gland Housings from the Outer Casing | [5 empty] | 140.1085 |  |  | 0
|  |  | Remove the front & rear outer gland housings and ‘U’ rings (Drawing No. 7093-12270, items 5 and 11) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Bolt on the radial and axial shaft locking devices to secure rotor to casing. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Camera Inspection of HP, IP and LP turbine internals | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Fit centering adaptor to rotor coupling face (7093-01430 item 84) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove exhaust flange nuts and dowels (leave four nuts tight) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Raise casing to the vertical position and secure in fixture (26) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the four lifting jacks (7093-01431 - item 159) under the pressure plate | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Lift pressure plate to just take weight of rotor and bolt to coupling face. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove outlet gland housing radial alignment keys | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Raise the rotor & remove front inner outlet gland housing axial keys (4). | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt, separate & remove the exhaust casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove inlet gland housing radial alignment keys | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Lower the rotor & rear inner gland down by 0.20mm & remove inlet inner gland housing axial keys (4). | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the two ‘U’ rings (Drawing No. 7093-12270, items 6 and 7 respectively) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install inner front erection frame assembly (Drawing No. 7093-01430, item 113) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Jack the rotor down with top jacks and columns 0.23 - 0.30mm such that the ‘U’ ring (Drawing No. 7093-12270, item 8) is compressed and no force is exerted on the inner casing retaining nut | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the locking plates from the inner casing retaining nut | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Loosen & remove the inner casing retaining nut | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Jack rotor back to its original position | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the eight radial keys, (Drawing No. 7093-12270, item 18) between the blade carrier and the outer casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Attach lifting bracket and shackle, (Drawing No. 7093-01430, items 86 and 106) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Lift the rotor and inner casing half way out of the main casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Attach two quarter circle brackets onto the inner casing and rear inner gland housing which locate the rotor to the blade carrier and inlet gland housing, (Drawing No. 7093-01430, item 105 and 109 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the rotor with inner casing and gland housings & lay down in the erection frame | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Dismantling of Blade Carrier & Gland Housings & Rotor Removal | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Adjust erection frame to support the blade carrier and gland housings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the casing and gland housings support brackets | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt & remove upper halves of gland housings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt & remove upper half of blade carrier | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove gland segments | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Removal of HP Rotor | [5 empty] | 140.1085
|  |  | Inspections | [5 empty] | 140.1085
|  |  | HP Rotor Inspection | [5 empty] | 140.1085
|  |  | Visual inspection of rotor | [5 empty] | 140.1085
|  |  | Visual inspection of Old rotor that is being replaced with new | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Gritblasting of rotor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Transport & setup old rotor at machine shop for rectification works | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT of Rotor (old rotor being replaced with refurbished rotor, NDT of new rotor has already been completed in Germany) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Removal of nominated seal strips | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Replace nominated seal strips | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Map postion of HP rotor balance weights fro future balancing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Row 1 Blades | [5 empty] | 140.1085
|  |  | Removal of row 1 turbine blades from old rotor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT of old rotor blade groove (after removing R1 blades) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | If cracking is found on row 1, row 2 and 3 are to be removed, groove modifed and installion of new blading is required. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machining of new root profile to Contractor design (possibly all 3 blade stages) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT of blade groove (post-machining) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Installation of blades on row 1 (days, grinding on nightshift) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Drilling and pinning of closing blade | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machining of shroud | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Installation of remaining seal strips | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Transport of old rotor back to site | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | HP Outer & Exhaust Casings (Inspect & Repair) | [5 empty] | 140.1085
|  |  | Inspection and cleaning of muff couplings and inlet pipes | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast exhaust casing and studs/nuts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast outer casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean all seal faces, flanges, etc. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT of Exhaust Casing | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT of Outer Casing | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Visual inspection & report of casings | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Inspection and machining of the muff couplings and inlet pipes on the HP outer casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Inspection and machining of the muff couplings and inlet pipes on the inlet pipes at the turbine floor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Blueing of keyways and parallel | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Contractor Machine Muff coupling faces with supplied NRG grinding machine | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Setup Spindle machine for grinding | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Grinding of all U seal faces and thrust tile faces inside outer casing and exhaust casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Installation of exhaust casing and measure | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure areas for 'U' ring reference measurements | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machine new casing U-seals, spread old u-seals to new size with preferred machine shop (Contractor will take control of all U-seal machining and spreading tasks) | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean, measure & record lengths of the exhaust casing bolts/nuts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean casing to pedestal axial and radial keys and keyways | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Prepare all inlet pipe welds for NDT as per NDT scope (Co-ordination is required from both Contractor and NRG Eng for linishing scope) | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | HP Inner Casing (Inspect & Repair) | [5 empty] | 140.1085
|  |  | Visual inspection & report | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT of HP blade carrier | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Nominate seal strips for removal | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Removal of nominated seal strips | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Installation of new seal strips and sizing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Weld repairs to cracked rivets (Contractor to nominate rivet repairs and work with boilermaker for schedule interface) | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the top half of blade carrier and bolt heat all bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Casing ovality & flange gap & shrouds checks | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Ream locating dowels (if applicable) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Transport to machine shop for U seal face rectification and witness mark (if agreed by both Contractor and NRG Eng) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure for 'U' ring compression | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | HP Front & Rear Outer Glands | [5 empty] | 140.1085
|  |  | Remove gland segments | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Visual inspection & report | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast outer gland housings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Prepare glands for NDT and reassembly | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT glands scope as per contract | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Gland ovality & flange gap checks | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Transport to machine shop and carry out rectification works if required (Contractor to organize machining works) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure for 'U' ring compressions | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove and re-install Gland seal pipework | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Note: when glands pipes are re-installed and bolted up by Contractor. Contractor and NRG schedule this scope to happen as a squential task (not in parrallel to other works on HP rebuild, cannot work around HP pedestal while boilermakers are welding in the area) | V | Contractor and NRG Sub Contractor |  | Note: when glands pipes are re-installed and bolted up by Contractor. Contractor and NRG schedule this scope to happen as a squential task (not in parrallel to other works on HP rebuild, cannot work around HP pedestals while boilermakers are welding in the area) |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | HP Front & Rear Inner Glands | [5 empty] | 140.1085
|  |  | Remove gland segments | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Visual inspection & report | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast inner gland housings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Prepare inner glands for NDT and reassembly | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT inner gland housings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Inner gland ovality & flange gap checks | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Transport for Machining | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machine U seal face's No 10 & 11 | V | Contractor |  | Note: Contractor to quote this estimated costs for machining works cost in TCE 2025 |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machine U seal face No 9 | V | Contractor |  | Note: Contractor to quote this estimated costs for machining works cost in TCE 2025 |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure for 'U' ring compressions | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reassembly | [5 empty] | 140.1085
|  |  | Pre Assembly Checks | [5 empty] | 140.1085
|  |  | Install inner gland housings to outer casing and perform assembly checks with spindle machine | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Set up lower inner gland housings in assembly frame | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install gland segments to inner gland housings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install inner casing and perform assembly checks (3 blocks x ??????mm) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install inner casing nut and fit new locking plates | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove Inner Casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Dismantle spindle machine | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt inner casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Set up lower inner casing in assembly frame | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install HP Rotor for final time | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform radial and axial blade and seal strip checks | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Assembly (rotor, casings & gland housings) | [5 empty] | 140.1085
|  |  | The HP Rotor will be in New condition, the HP Inner casing scope does need to wait on the HP rotor returning to site (like on a normal Overhaul of stage 1 balde removal). This new rotor scope task can be started as soon as the Inner casing is prepped to except the Rotor. |  |  |  | Schedule for sequential task after Inner casing is ready. |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install top half and tighten inner casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform radial and axial bump checks (confirm and report measurements) | F | Contractor |  | this is to confirm last assembly position. |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Setup glands and perform radial and axial seal strip checks | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install and Tighten inner gland housing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install clamping jigs and plates to secure rotor and casings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install 'U' rings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install HP rotor and casings into outer casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install inner casing radial keys and reconfirm key clearances | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Bolt coupling to pressure plate | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the radial keys to the inner gland housing and reconfirm key clearances | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install and tighten the inner casing nut (jack rotor down by 0.20 mm) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Final install the three locking plates | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Jack rotor up by 0.20 mm | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove erection clamp from inner casing (item 113) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Jack rotor down by 0.20 mm from natural position | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the inner gland axial keys | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install exhaust casing and outlet gland 'U' rings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install and partly tighten the exhaust casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the axial & radial keys to inner outlet gland | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Lift HP turbine and lay back on erection stands | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install outer gland 'U' rings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reposition the two roller blocks under the HP rotor front and rear journal areas | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the radial and axial shaft locking devices from rotor to casing. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure and record the run out of the rotor and outer casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install and tighten the exhaust casing bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform radial and axial bump checks and re-centralise | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the lower outer gland housings and centralise | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install gland segments and measure axial and radial clearances | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install & tighten upper outer gland housings (Temporary installation) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Final axial bump check | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install shaft raising gear and support rotor (rotor to be pushed forward) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Final Installation (HP Turbine) (Refer to 7.2.1 and 7.2.2 of Scope of Work) | [5 empty] | 140.1085
|  |  | HP rotor and casing will be checked for correct clearances both axially and radially, this could include changing postion of the HP casing. | [5 empty] | 140.1085 |  |  | 37759.2321
|  |  | Camera inspection of HP exhaust legs all the way down to RHB's valves (Cold reheat Non returns) | F | Contractor |  | Check for debris under exhaust flange covers (critical for boiler runup) |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install "U" seals blue and final checks for turbine return to pedestals | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Return turbine to bearing pedestals | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-38 | 8.55.6.125 | Remove and inspect barring mechanism. (new design barring mechanism in place) | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
|  |  | Tighten exhaust flanges & Lower gland Pipes | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install No 1 Bearing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Jack casing and Install Number 2 bearing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-48 | 8.55.6.126 | Align and install barring mechanism. | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
|  |  | Remove top half outer glands (For axial bump checks) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform and record axial bump check (HP Turbine Only) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-51 | 8.55.6.176 | Inspect turning gear valve internals, remove actuator and hand over to Principal, repair if necessary after blueing valve seats.. | F | Contractor |  | In 2026 Overhaul | 24 | 140.1085 | 3362.6032 |  |  |  |  | 0
00173164/00001 | 28243985-51 | 8.55.6.132 | Clean, inspect, blue check turning oil valve | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  |  | 0
00173164/00001 | 28243985-64 | 8.55.6.141 | Replace internal and external o-rings and Shaft seal | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243985-64 | 8.55.6.156 | Bled steam actuators S91, S86, S78, S81 replace seals and o-rings | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 |  |  | Fit coupling bolts HP-IP & IP-LP | O | Contractor |  | Not in current 2026 scope | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 |  |  | Tighten HP/IP coupling including concentricity checks | O | Contractor |  | Not in current 2026 scope | 21 | 140.1085 | 2942.2778 |  |  |  |  | 0
00173164/00001 |  |  | Tighten IP/LP coupling including concentricity checks | O | Contractor |  | Not in current 2026 scope | 21 | 140.1085 | 2942.2778 |  |  |  |  | 0
00173164/00001 |  |  | Fit windage plates to the couplings | O | Contractor |  | Not in current 2026 scope | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
|  |  | Setup and tighten Muff Coupling No 2 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Setup and tighten Muff Coupling No 1 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Setup and tighten Muff Coupling No 3 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Setup and tighten Muff Coupling No 4 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-94 | 8.55.6.170 | Only if replacing oil, Refill main tank with new supplied turbine oil (fill date to be negoiated to match Contractor schedule) | F | Contractor |  | New oil being supplied, Contractor to remove oil and fill tank with new. | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
|  |  | Reinstall outer gland top half's | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-94 | 8.55.6.171 | Refill main oil tank with oil | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00004 | 28243979-47 | 8.56.6.009 | Prepare the Generator and Stator for robotic inspection performed by Contractor. | F | Contractor |  | In 2026 Overhaul (Robotic inspection required for Minor Gen Overhaul) | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00004 | 28243986-04 | 8.56.6.010 | Remove Number 4 Bearing Pedestal Cover | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  |  | 0
00173164/00004 | 28243986-08 | 8.56.6.012 | Remove No 4 bearing bridge and top half bearing | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  |  | 0
00173164/00004 | 28243986-19 | 8.56.6.015 | Perform Bearing 4 Stripdown Measurements (Top lead check etc) | F | Contractor |  | In 2026 Overhaul | 42 | 140.1085 | 5884.5556 |  |  |  |  | 0
|  |  | HP and IP Casing Horn Soft Foot, Adjust Casings and recheck with Vertical Bump | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Final rollout of IP & HP Turbine with plates fitted | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reconnect Auxiliary and Gland Steam Pipework (welding Contractor) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-47 | 8.56.6.075 | 16.Robotic inspection of Stator and rotor | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
|  |  | Transport to machine shop for U seal face rectification and witness mark | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform Turbine drive train balance (perform if required from vibration reports) |  | Sub-Contractor |  | During run up. Unit 2 Vibration has been within specification since 2017 Overahul.
140.1085
|  |  | IP Turbine (Refer to 7.7 in Scope of Work) | [5 empty] | 140.1085 |  |  | 4483.471
|  |  | IP Turbine Overhaul | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Dismantling | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Disconnect & remove the IP inlet, exhaust, gland steam & bled steam pipe work | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-52 | 8.56.6.093 | Seal Oil Flush | F | Contractor |  | In 2026 Overhaul | 32 | 140.1085 | 4483.471 |  |  |  |  | 0
|  |  | Install the IP outer casing support bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform casing to rotor bump checks, if required for axail references (is there any reason to perform this??) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the upper centering pins | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt the IP outer casing bolts/nuts and remove the dowel pins | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the large nuts (crane) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure and record the IP outer casing flange gap before jacking the casing apart | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the IP outer casing to lay down area | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt and remove the IP inner casing bolts/nuts and dowel pins | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure and record the inner casing flange gap before jacking the casing apart | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the IP upper inner casing to lay down area | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure & record the radial & axial clearances of the IP rotor to the IP casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the IP rotor to the lay down area and install the temporary stub shaft to the rotor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the lower centering pins | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove lower IP inner casing to lay down area | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Inspection, Testing & Repairs | [5 empty] | 140.1085
|  |  | IP Rotor | [5 empty] | 140.1085
|  |  | Visual inspection of old rotor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Gritblast IP rotor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the IP rotor as per GPS-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Map Position of balnce weights for future balancing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean the IP components (e.g. coupling bolts, coupling faces, etc.) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Row 1 Blades Left and Right Flow | [5 empty] | 140.1085
|  |  | Transport of rotor to machine shop | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Setup of rotor at machine shop | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Removal of row 1 turbine blades for blade root inspection | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT of blade groove (pre-machining) NDT results determine if move blades need removing? | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | If cracking is found on row 1, row 2 and 3 are to be removed, groove modifed and installion of new blading is required. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machining of new root profile to suit new design blading | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT of blade groove (post-machining) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Installation of blades on row 1 (days, grinding on nightshift) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Drilling and pinning of closing blade | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machining of shroud | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Installation of remaining seal strips | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Transport of rotor back to site | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Outer Casing | [5 empty] | 140.1085
|  |  | Visual inspection & report on the IP upper casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Visual inspection & report on the IP lower casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean, measure & record all components, including 'L' rings seats, keys, etc. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast the outer casing bolts & nuts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean, measure & record the IP outer casing bolts/nuts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT outer casing studs & nuts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean the casing to pedestal axial and radial keys | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean all the IP steam flanges | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the IP upper casing as per GPS-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the IP lower casing as per GPS-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machine lower half steam inlet grooves (if required, show costing in TCE) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machine upper half steam inlet grooves - Y Piece (if required, Show costing in TCE) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Prepare all the IP inlet pipe welds for NDT as per GPO-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the IP turbine pipe welds as per GPO-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Inner Casings | [5 empty] | 140.1085
|  |  | Visual inspection & report on the IP inner upper casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Visual inspection & report on the IP inner lower casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the angle rings from the IP inner upper casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast the IP inner upper casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the angle rings from the IP inner lower casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast the IP inner lower casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the IP inner upper casing as per GPO-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the IP inner lower casing as per GPO-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machine IP inner upper casing (offsite) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Machine IP inner lower casing (offsite) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Removal of nominated seal strips | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Installation & sizing of seal strips | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean, measure & record 'L' ring clearances | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean, measure & record the eccentric bushes, pins and keys diameters | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Replace the inner casing bolts (if applicable) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Replace the inner casing thermocouples | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remedial work (e.g. replacement of 'L' rings, etc.) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Casing ovality & flange gap checks | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Inner and Outer Glands | F |  |  |  |  | 140.1085
|  |  | Remove the IP gland segments | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Visual inspection & report on the IP glands and segments | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Prepare the IP glands and segments for NDT | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the IP glands, etc. as per GPO-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform the IP gland ovality & flange gap checks | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Removal of nominated seal strips | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Installation & sizing of seal strips | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the IP gland segments | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Assembly | F |  |  |  |  | 140.1085
|  |  | Install the IP inner casing into the IP outer casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install top half inner casing for ovailty check & bolt heat | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform gap & ovality checks | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install dummy shaft into inner casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Set up millitrons or dial indicators to the dummy shaft | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the IP outer casing & tighten 50% of the casing bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform casing alignments checks and make corrections | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install and secure alignment pins/bushes | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the top half of outer casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the top half of the IP inner casing & the dummy shaft | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Adjust the inner casing alignment plates and keys (if required) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | The IP Rotor will be in New condition. This rotor installation scope task can be started as soon as the Inner casing is prepped to except the IP Rotor. | [5 empty] | 140.1085
|  |  | Install the IP rotor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure and record the seal & blade clearances (axial & radial) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the IP upper inner casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Tighten the IP inner casing bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Cool out period | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure and retighten the bolts (if required) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Cool out period | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the IP outer casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Tighten the IP outer casing bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Cool out period | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform the IP rotor to casing bump checks (radial & axial) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Adjust the alignment plates & keys (if required) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure and retighten the outer casing bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install all the pipe work to the IP turbine | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Connect all instruments to IP outer casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | LP Turbine | [5 empty] | 140.1085
|  |  | LP Dismantling | [5 empty] | 140.1085
|  |  | Unbolt the LP outer hood cover | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt and remove the LP upper shaft gland covers | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the hood cover to the loading bay | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Erect scaffolds under the LP turbine to access the lower centering pins, radial keys and exhaust diffusers and inlet pipe bellows | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install support angle iron around the LP turbine half joint (if required) | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the access platform/half joint covers | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform a bump check of the LP inner casings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the LP upper centering pins | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt & remove LP upper casing No. 2 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Unbolt & remove the LP upper inner casing No.1 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure & record the radial & axial clearances of the LP rotor to LP casings and glands | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove the LP Rotor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove both "North and South" outer shrouds for access to inner and outer casing bellows (U1 bellows are not being replaced, only the outer bellows will require NDT and the inner bellows will be visual inspection) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | LP Inspection, Testing & Repairs | [5 empty] | 140.1085
|  |  | LP Rotor | [5 empty] | 140.1085 |  |  | 22417.3548
|  |  | Visual inspection of LP rotor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast the LP rotor (use NRG approved blast medium) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove L-0 / L-1 / L-2 locking plates | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove L-0 blades | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove L-1 blades | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove L-2 blades | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Cleaning of locking ring grooves (blast groove slot) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Cleaning of LP blades after removal (blast LP blades) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the LP rotor as per GPS-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT L-0 / L-1 / L-2 locking grooves and fir tree grooves | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | LP Fir tree Rectification work- grinding of all findings after NDT on all 6 rows (use past hours as baseline hours) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT of L-0 / L-1 / L-2 blades after removal | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reinstallation of L-0 blades | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reinstallation of L-1 blades | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reinstallation of L-2 blades | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reinstallation & welding of L-0 / L-1 / L-2 locking plates |  | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Welding of locking plates to be a combined effort (Contractor and NRG Engineering to sign off) |  | NRG Subcontractor |  |  |  |  | 0 |  |  |  |  | 0
|  |  | Clean the LP components (e.g. coupling bolts, coupling faces, etc.) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243986-04 | 8.55.6.181 | Remove the bearing pedestal covers from bearings 1, 2, 3 & 4 including oil labyrinths | F | Contractor |  | In 2026 Overhaul | 110 | 140.1085 | 15411.9315 |  |  |  |  | 0
00173164/00001 | 28243986-08 | 8.55.6.184 | Remove the bearing bridges and top halves of bearings 1, 2, 3 & 4 | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243986-19 | 8.55.6.197 | Clean, visually inspect and measure the bearing clearances of bearings by lead check only on dissemessbly (1 - 4 bearings) and thrust pads | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
|  |  | LP Casing No. 2 (Refer to 7.4.2 in Scope of Work) | [5 empty] | 140.1085 |  |  | 11629.0028
|  |  | Visual inspection & report on the LP 2 upper casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Visual inspection & report on the LP 2 lower casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast the LP upper casing 2 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT casing (LP upper half) as per GPS-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean, measure & record all components, including keys, etc. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean the casing bolts and nuts and record the bolt lengths | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean the LP casing half joints flanges | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the LP lower casing as per GPS-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243986-27 | 8.55.6.198 | Replace the brass sealing strips on oil wipers only as required | V | Contractor | allow for 6 off oil wipers | In 2026 Overhaul | 65 | 140.1085 | 9107.0504 |  |  |  |  | 0
00173164/00001 | 28243985-38 | 8.55.6.200 | Remove and inspect mechanical barring mechanism | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  |  | 0
|  |  | LP Casing No. 1 | [5 empty] | 140.1085 |  |  | 0
|  |  | Visual inspection & report on the LP 1 upper casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Visual inspection & report on the LP 1 lower casing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast the LP upper casing 1 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the LP 1 upper casing as per GPS-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Prepare the lower LP casing for NDT | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the LP 1 lower casing as per GPS-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean, measure & record all components, including keys, etc. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean, measure & record the LP casing bolts/nuts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean the LP turbine half joints flanges | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | LP Outer Glands (Refer to 7.4.6 in Scope of Work) | [5 empty] | 140.1085 |  |  | 7005.4234
|  |  | Remove the gland segments | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-48 | 8.55.6.202 | Install new automatic barring gear when no.3 bearing lid is on for final time. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243986-42 | 8.55.6.105 | Assemble the bearings covers for oil flushing | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
|  |  | Prepare the LP glands for NDT | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the LP gland housings as per GPO-55-001 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the LP gland segments | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform the LP gland ovality & flange gap checks | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | LP Reassembly | [5 empty] | 140.1085 |  |  | 0
|  |  | Replace outer shrouds after the replacement of LP inner to outer casing bellows | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install No. 4 lower turbine bearing |  | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the LP Rotor | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform seal & blade clearance checks (axial & radial) on the LP turbine | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the exhaust diffusers | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the LP upper gland housings | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the LP inner casing 1 and tighten the bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Cool out period | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Retighten the LP inner casing bolts (if required) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the LP inner casing 2 | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform the LP final bump checks and adjustments | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove scaffolds from the LP turbine |  | Subcontractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install the outer hood cover | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Turbine General | [5 empty] | 140.1085
|  |  | HP Stop Valves and Control Valves (Refer to 7.5 in Scope of Work) | [5 empty] | 140.1085
|  |  | HP Stop Valve No. 1 | [5 empty] | 140.1085 |  |  | 5604.3387
00173164/00001 | 28243986-45 | 8.55.6.108 | Set up the differential expansion devices and internal instrumentation | F | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243986-47 | 8.55.6.110 | Refit the external instrumentation | F | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243986-42 | 8.55.6.115 | Prepare bearings for oil flushing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243979-52 | 8.55.6.116 | Oil flush seal oil system | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243986-45 | 8.55.6.120 | Differential expansion set up (NRG) | F | NRG/Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243986-47 | 8.55.6.122 | Refit external instrumentation | F | NRG/Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
Service Order Number/Release | Work Order and Work Order Task Combined | Scope No. | Unit 2 2026 Turbine Scope Development - Activity description | Scope Type | Task responsibility (Contractor/ NRGGOS/ Others) | Variable Scope Measurement Definition | Comment | Estimated Hours | Gang rate $/hr | Estimated Total Cost | Notes |  | Estimated Hours | Gang rate $/hr | Estimated Total Cost (excl.GST) | Notes | Week 1 - Actual Hours | Week 1 - Actual Total Cost | Week 2 - Actual Hours | Week 2 - Actual Total Cost | Week 3 - Actual Hours | Week 3 - Actual Total Cost | Week 4 - Actual Hours | Week 4 - Actual Total Cost | Week 5 - Actual Hours | Week 5 - Actual Total Cost | Week 6 - Actual Hours | Week 6 - Actual Total Cost | Week 7 - Actual Hours | Week 7 - Actual Total Cost | Week 8 - Actual Hours | Week 8 - Actual Total Cost | Week 9 - Actual Hours | Week 9 - Actual Total Cost | Week 10 - Actual Hours | Week 10 - Actual Total Cost | Week 11 - Actual Hours | Week 11 - Actual Total Cost | Variation Hours | Variation Amount | Total - Actual Hours | Total - Actual Total Cost | Total - Actual Gang Rate | Percentage of Hours Complete | Percentage of Cost Used | Task Complete | Forecast Cost for Completion of Project
|  |  | HP Stop Valve No. 2 | [5 empty] | 140.1085 |  |  | 25569.7954
00173164/00001 | 28243980-04 | 8.52.6.005 | Remove casing to bearing pedestal keys (this task to be discussed with NRG Engineering before removal) | F | Contractor |  | In 2026 Overhaul | 90 | 140.1085 | 12609.7621 |  |  |  |  | 0
00173164/00001 | 28243980-05 | 8.52.6.011 | Install shaft raising equipment and support the HP and IP rotors | F | Contractor |  | In 2026 Overhaul | 28 | 140.1085 | 3923.0371 |  |  |  |  | 0
00173164/00001 | 28243980-14 | 8.52.6.155 | Install the radial and axial bearing/pedestal/casing keys | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  |  | 0
00173164/00001 | 28243980-15 | 8.52.6.159 | Check HP Shaft to pedestal measurements (radial measurements to be compared to last Overhaul records) | F | Contractor |  | In 2026 Overhaul | 16 | 140.1085 | 2241.7355 |  |  |  |  | 0
00173164/00001 | 28243980-17 | 8.52.6.162 | Engage HP-IP & IP-LP Spiggots, install temporary bolts | O | Contractor |  | This task is not in current scope for 2026, as we are not splitting the HP,IP and LP front to be performed only by Principal Superintendant approval) | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243980-18 | 8.52.6.163 | Install Axial Keys on HP Turbine & Set | F | Contractor |  |  | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
|  |  | HP Stop Valve No. 3 | [5 empty] | 140.1085 |  |  | 11068.569
00173164/00001 | 28243980-19 | 8.52.6.164 | Check Axial Position of HP, IP & LP Turbine | F | Contractor |  |  | 12 | 140.1085 | 1681.3016 |  |  |  |  | 0
00173164/00001 | 28243986-31 | 8.52.6.200 | Perform coupling alignment of the HP/IP, IP/LP rotors | O | Contractor |  | Only if required. | 21 | 140.1085 | 2942.2778 |  |  |  |  | 0
00173164/00001 | 28243980-25 | 8.52.6.169 | Perform Axial Bump Test (all coupled total float) | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243980-26 | 8.52.6.171 | Remove Number 2 and fit thrust pads and perform thrust clearance check | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243980-27 | 8.52.6.172 | Install and perform run out on Stub Shaft | F | Contractor |  | In 2026 Overhaul | 6 | 140.1085 | 840.6508 |  |  |  |  | 0
00173164/00001 | 28243980-28 | 8.52.6.201 | Install the main oil pump including alignments, etc. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694
|  |  | HP Stop Valve No. 4 | [5 empty] | 140.1085 |  |  | 13170.196
00173164/00001 | 28243980-29 | 8.52.6.173 | Adjust casings axial setting for positive and negative clearances, grind keys and fit | F | Contractor |  | In 2026 Overhaul | 21 | 140.1085 | 2942.2778 |  |  |  |  | 0
00173164/00001 | 28243980-30 | 8.52.6.174 | Initial Rollout Check IP & HP Turbine | O | Contractor |  | This scope is only required if changes are needed due to Turbine shaft to bearing pedestal measurements being different. Please put hours in the TCE to reflect this in case this task is performed. | 24 | 140.1085 | 3362.6032 |  |  |  |  | 0
00173164/00001 | 28243986-52 | 8.52.6.178 | Turbine on barring | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243983-02 | 8.53.6.004 | Remove the radial and axial keys (IP casing to bearing pedestals) check clearances are within specfication. | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243983-03 | 8.54.6.028 | Measure and record reference data as required to determine the correct procedure for reassembly. | F | Contractor |  |  | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
00173164/00001 | 28243983-04 | 8.54.6.029 | Measure and record rotor in relationship to pedestal, compare figures to 2019 outage. | F | Contractor |  |  | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
|  |  | HP Control Valves | [5 empty] | 140.1085
|  |  | HP Control Valve No. 1 | [5 empty] | 140.1085 |  |  | 10087.8097
00173164/00001 | 28243983-05 | 8.54.6.030 | Clean and inspect coupling faces. | F | Contractor |  |  | 11 | 140.1085 | 1541.1931 |  |  |  |  | 0
00173164/00001 | 28243984-01 | 8.54.6.031 | Check hood spray piping nozzles, supports, bled steam drains and unions. | F | Contractor |  |  | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
00173164/00001 | 28243984-02 | 8.54.6.032 | Replacement of LP outer hood bursting discs (4 off). | F | Contractor |  |  | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243984-04 | 8.54.6.048 | Clean, measure and record all key fits. | F | Contractor |  |  | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243984-07 | 8.54.6.049 | Visual inspection & report on the LP glands | F | Contractor |  |  | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
00173164/00003 | #N/A |  | Off site machining of HP valve bodies, 8 off valves | V | Contractor |  | In 2026 Overhaul, will need to be costed in TCE for offsite machining. |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00003 | 28243981-05 | 8.55.6.001 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
|  |  | HP Control Valve No. 2 | [5 empty] | 140.1085 |  |  | 32925.4899
00173164/00003 | 28243981-06 | 8.55.6.002 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-07 | 8.55.6.003 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  |  | 0
00173164/00003 | 28243981-08 | 8.55.6.004 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-09 | 8.55.6.005 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-10 | 8.55.6.006 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  |  | 0
00173164/00003 | 28243981-11 | 8.55.6.007 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-12 | 8.55.6.008 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
|  |  | HP Control Valve No. 3 | [5 empty] | 140.1085 |  |  | 35727.6593
00173164/00003 | 28243981-13 | 8.55.6.009 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  |  | 0
00173164/00003 | 28243981-14 | 8.55.6.010 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-15 | 8.55.6.011 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-16 | 8.55.6.012 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  |  | 0
00173164/00003 | 28243981-17 | 8.55.6.013 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-18 | 8.55.6.014 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-19 | 8.55.6.015 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 60 | 140.1085 | 8406.5081 |  |  |  |  | 0
|  |  | HP Control Valve No. 4 | [5 empty] | 140.1085 |  |  | 31524.4052
00173164/00003 | 28243981-20 | 8.55.6.016 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-21 | 8.55.6.017 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-22 | 8.55.6.018 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  |  | 0
00173164/00003 | 28243981-23 | 8.55.6.019 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-24 | 8.55.6.020 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-25 | 8.55.6.021 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  |  | 0
00173164/00003 | 28243981-26 | 8.55.6.022 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
|  |  | IP Stop Valves and Control Valves | [5 empty] | 140.1085
|  |  | IP Stop Valve No. 1 | [5 empty] | 140.1085
|  |  | Off site machining of IP valve bodies, 8 off valves | V |  |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul valve | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Check seat condition, lap/grind seat as required | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Stop Valve No. 2 | [5 empty] | 140.1085
|  |  | Remove valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul valve | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Check seat condition, lap/grind seat as required | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Stop Valve No. 3 | [5 empty] | 140.1085
|  |  | Remove valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul valve | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Check seat condition, lap/grind seat as required | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Stop Valve No. 4 |  | Contractor |  |  |  | 140.1085
|  |  | Remove valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul valve | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Check seat condition, lap/grind seat as required | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Control Valves | [5 empty] | 140.1085
|  |  | IP Control Valve No. 1 | [5 empty] | 140.1085
|  |  | Remove valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul valve | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Check seat condition, lap/grind seat as required | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Control Valve No. 2 | [5 empty] | 140.1085
|  |  | Remove valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul valve | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Check seat condition, lap/grind seat as required | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Control Valve No. 3 | [5 empty] | 140.1085
|  |  | Remove valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul valve | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Check seat condition, lap/grind seat as required | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | IP Control Valve No. 4 | [5 empty] | 140.1085
|  |  | Remove valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul actuator | F |  |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul valve | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Check seat condition, lap/grind seat as required | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install valve and actuator | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | HP and IP steam strainers | [5 empty] | 140.1085
|  |  | IP Steam Strainers (4 off) | [5 empty] | 140.1085
|  |  | To be confirmed-Replace strainer with new item (inspect old strainer for damage) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove IP strainers | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast, clean and inspect IP strainers | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the IP strainers in accordance with Principal’s Procedure | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reassemble IP strainers | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | HP Steam Strainers (4 off) | [5 empty] | 140.1085
|  |  | To be confirmed-Replace strainer with new item (inspect old strainer for damage) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove HP strainers | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Sandblast, clean and inspect HP Strainers | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT the HP strainers in accordance with Principal’s Procedure | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reassemble HP strainers | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Lube oil system | [5 empty] | 140.1085
|  |  | Main Oil Pump (Refer to 7.6.1 in Scope of Works) | [5 empty] | 140.1085 |  |  | 32224.9476
00173164/00003 | 28243981-27 | 8.55.6.023 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00003 | 28243981-28 | 8.55.6.024 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  |  | 0
00173164/00003 | 28243981-29 | 8.55.6.025 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  |  | 0
00173164/00003 | 28243981-30 | 8.55.6.026 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-31 | 8.55.6.027 | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  |  | 0
00173164/00003 | 28243981-32 | 8.55.6.028 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-33 | 8.55.6.029 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 52 | 140.1085 | 7285.6403 |  |  |  |  | 0
00173164/00003 | 28243981-34 | 8.55.6.030 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
|  |  | Oil Labyrinths (1 - 4) | [5 empty] | 140.1085 |  |  | 2802.1694
00173164/00003 | 28243981-35 | 8.55.6.031 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
|  |  | Turbine Auxiliary Oil Pumps (Two off AC and One DC Pumps) | [5 empty] | 140.1085 |  |  | 10227.9181
00173164/00003 | 28243981-36 | 8.55.6.032 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  |  | 0
00173164/00003 | 28243981-37 | 8.55.6.033 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-38 | 8.55.6.034 | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  |  | 0
|  |  | Auxiliary Works (Refer to 7.6 Lube Oil System in Scope of Works) | [5 empty] | 140.1085
|  |  | Turning Gear/ Barring Gear | [5 empty] | 140.1085 |  |  | 21997.0294
00173164/00003 | 28243981-39 | 8.55.6.035 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-40 | 8.55.6.036 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 52 | 140.1085 | 7285.6403 |  |  |  |  | 0
00173164/00003 | 28243981-41 | 8.55.6.037 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00003 | 28243981-42 | 8.55.6.038 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00003 | 28243981-43 | 8.55.6.039 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  |  | 0
|  |  | Install new design barring mechanism as per customers instructions in scope document. | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Overhaul Emergency Shut Off Valve | [5 empty] | 140.1085 |  |  | 12329.5452
00173164/00003 | 28243981-44 | 8.55.6.040 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-45 | 8.55.6.041 | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  |  | 0
00173164/00003 | 28243981-46 | 8.55.6.042 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
|  |  | Overhaul Turning Oil Valve | [5 empty] | 140.1085 |  |  | 12889.979
00173164/00003 | 28243981-47 | 8.55.6.043 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 52 | 140.1085 | 7285.6403 |  |  |  |  | 0
00173164/00003 | 28243981-48 | 8.55.6.044 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00003 | 28243981-49 | 8.55.6.045 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
|  |  | Gland Steam Dump Valve | [5 empty] | 140.1085 |  |  | 10227.9181
00173164/00003 | 28243981-50 | 8.55.6.046 | Remove valve and actuator | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  |  | 0
00173164/00003 | 28243981-51 | 8.55.6.047 | Overhaul actuator | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-52 | 8.55.6.048 | Remove actuator spool and cam for inspection (check spool and cam conditon) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  |  | 0
|  |  | Gland Steam Control Valve | [5 empty] | 140.1085 |  |  | 15692.1484
00173164/00003 | 28243981-53 | 8.55.6.049 | Overhaul valve | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00003 | 28243981-54 | 8.55.6.050 | Check seat condition, lap/grind seat as required | F | Contractor |  | In 2026 Overhaul | 52 | 140.1085 | 7285.6403 |  |  |  |  | 0
00173164/00003 | 28243981-55 | 8.55.6.051 | Install valve and actuator | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
|  |  | Bled Steam Extraction Actutors -S91, S86, S78 , S81. | [5 empty] | 140.1085 |  |  | 4203.254
00173164/00003 | 28243981-56 | 8.55.6.052 | Install oil strainers at actuator inlet pipework for testing/remove strainers after testing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-02 | 8.55.6.113 | Inspect MOP pump coupling for wear. | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
00173164/00001 | 28243985-03 | 8.55.6.114 | Record insitue measurements of pump shaft run out, | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
|  |  | Governing System (Hydraulic system refurbishment) | [5 empty] | 140.1085
|  |  | Contractor technican to help Overhaul the hydraulic system (spares required) | [5 empty] | 140.1085 |  |  | 13660.5756
00173164/00001 | 28243985-04 | 8.55.6.115 | Check end float of pump thrust bearing. | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
00173164/00001 | 28243985-06 | 8.55.6.117 | Measure and record run out of extension shaft and eccentricity disc. Check tightness of the bolting of the extension shaft. | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
00173164/00001 | 28243985-07 | 8.55.6.118 | Replace with new complete pump if required | F | Contractor |  | Replace Main oil pump if required | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
00173164/00001 | 28243985-09 | 8.55.6.120 | MOP coupling alignment | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-10 | 8.55.6.121 | Remove motors and handover to Principal | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
00173164/00001 | 28243985-11 | 8.55.6.122 | Check pump couplings, inspect pump endfloat condition | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
00173164/00001 | 28243985-46 | 8.55.6.123 | Reinstall motors and align to pump | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
00173164/00001 | 28243985-47 | 8.55.6.124 | Check seal clearance prior to removal. | F | Contractor |  | In 2026 Overhaul | 2 | 140.1085 | 280.2169 |  |  |  |  | 0
00173164/00001 | 28243985-49 | 8.55.6.175 | The Contractor to verify manual and automatic operation at the completion of Turbine assembly | F | Contractor |  | In 2026 Overhaul | 2 | 140.1085 | 280.2169 |  |  |  |  | 0
00173164/00001 | 28243985-41 | 8.55.6.128 | Remove and replace emergency shut off valve | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
00173164/00001 | 28243985-42 | 8.55.6.129 | Clean, inspect, overahul and blue check emergency shut off valve | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00001 | 28243985-43 | 8.55.6.130 | Repair seat if damaged | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243985-54 | 8.55.6.131 | Remove inspect and replace turning oil valve | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
00173164/00001 | 28243985-53 | 8.55.6.133 | Repair seat if damaged | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  |  | 0
|  |  | Contractor Commissioning Engineer for Governor setup setup | [5 empty] | 140.1085 |  |  | 840.6508
00173164/00001 | 28243985-56 | 8.55.6.134 | Remove actuator | F | Contractor |  | In 2026 Overhaul | 6 | 140.1085 | 840.6508 |  |  |  |  | 0
|  |  | Jacking Oil System (Refer to 7.6.5 in Scope of Works) | [5 empty] | 140.1085 |  |  | 21716.8125
00173164/00001 | 28243985-57 | 8.55.6.135 | Strip and inspect valve and carry out any repairs | F | Contractor |  | In 2026 Overhaul | 21 | 140.1085 | 2942.2778 |  |  |  |  | 0
00173164/00001 | 28243985-58 | 8.55.6.136 | Assembly Valve and actutor | F | Contractor |  | In 2026 Overhaul | 31 | 140.1085 | 4343.3625 |  |  |  |  | 0
00173164/00001 | 28243985-59 | 8.55.6.137 | Remove actuator | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243985-60 | 8.55.6.138 | Strip and inspect valve and carry out any repairs | F | Contractor |  | In 2026 Overhaul | 21 | 140.1085 | 2942.2778 |  |  |  |  | 0
00173164/00001 | 28243985-61 | 8.55.6.139 | Assembly Valve and actutor | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00001 | 28243985-63 | 8.55.6.140 | Disassemble Actutors | F | Contractor |  | In 2026 Overhaul | 42 | 140.1085 | 5884.5556 |  |  |  |  | 0
|  |  | Main Oil Tank and Piping (Refer to 7.6.6 in Scope of Works) | [5 empty] | 140.1085 |  |  | 18914.6431
00173164/00001 | 28243985-65 | 8.55.6.142 | Reassemble actuator | F | Contractor |  | In 2026 Overhaul, Commisioning Engineer to test operation of bled steam actuators. | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
00173164/00001 | 28243985-67 | 8.55.6.143 | Clean control oil inlet filters | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
|  |  | Drain main oil tank (Contractor setup bund for possible oil spill around tank) | F | Contractor |  | Setup Oil spill bund in 2025 |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-69 | 8.55.6.144 | Inspect low vacuum trip device (replace diaphram) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-70 | 8.55.6.145 | Check starting device followup pistons (do these require spares?) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-71 | 8.55.6.146 | Over speed trip device, | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-72 | 8.55.6.147 | Electro-hydraulic convertor (EHC) Relpace spool and Bush | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-73 | 8.55.6.148 | Solenoid valves , 9 off | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-74 | 8.55.6.149 | Starting and load limit device (starting device) | F | NRG/Contractor |  | NRG Electricians Overhaul the electric motor |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243985-75 | 8.55.6.150 | Hydraulic speed governor (speeder gear) | F | NRG/Contractor |  | NRG Electricians Overhaul the electric motor |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243985-76 | 8.55.6.151 | Thrust bearing trip (at no 2 bearing) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
|  |  | A and B Turbine Oil Coolers | [5 empty] | 140.1085
|  |  | Dismantle Turbine oil coolers A and B | F | Contractor |  | Allow 10 days for cleaning and transport. |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Dismant treated water piping to coolers | F | Contractor |  | Allow 10 days for cleaning and transport. |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Clean A amd B cooler tube bundles as per Contractor procedure used onsite during previously overhuals. | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Recoat internal water box if required after clreaning and inspection. | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Inspect and Overhaul Turbine oil cooler 3 way valve. | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reassemble treated water and oil pipework to coolers | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Generator (Refer to 7.7 of Scope of Works) | [5 empty] | 140.1085
|  |  | Generator Major Overhaul. | [5 empty] | 140.1085
|  |  | Generator Minor Overhaul in 2026 only. | [5 empty] | 140.1085
|  |  | Exciter | F | Contractor |  |  |  | 140.1085 |  |  | 18214.1008
|  |  | Dismantling | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-77 | 8.55.6.152 | Over speed trip mechanisms, 2 off on turbine shaft | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-78 | 8.55.6.153 | Follow up piston assembliesCheck integrity of HP and IP followup pistons (for control valving) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
|  | 8.56.6.003 | Inspection & Testing | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-79 | 8.55.6.154 | Overspeed Micro switches | F | NRG/Contractor |  | NRG Electricians check the switches |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243985-80 | 8.55.6.155 | Clean & inspect over-speed bolts & trip mechanism | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-99 | 8.55.6.157 | Setup Main Turbine and Governor to correct OEM specification (check set up of control valve actuators, bled steam actuators), this standard and specification will be discussed with the Turbine Superintendent before work commences. | V | Contractor |  | Setup control oil/governor system as soon as possible (while Contractor fitters are available for any changes to control actuators) | 0 |  | 0 |  |  |  |  | 0
00173164/00001 | 28243985-81 | 8.55.6.159 | Remove clamps and inspect jacking oil pipework / manifold for rubbing and cracks. (this scope is to be an ITP and signed off before leaving site) | F | SubContractor |  | In 2026 Overhaul | 70 | 140.1085 | 9807.5927 |  |  |  |  | 0
|  |  | Generator Major Overhaul. | [5 empty] | 140.1085
|  |  | Generator Minor Overhaul in 2026 only. | [5 empty] | 140.1085 |  |  | 52120.35
|  | 8.56.6.008 | Dismantling | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-82 | 8.55.6.160 | Replace small bore pipework with new (sub Contractor to work in with Contractor schedule) | F | SubContractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-83 | 8.55.6.161 | Strip and inspect manifold by-pass valve. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-84 | 8.55.6.162 | Replace jacking oil hoses on all (7) bearings. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
|  |  | H2 Cooler Pipework Water Side Dismantle & Unbolt | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove H2 Coolers | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243985-86 | 8.55.6.163 | IInstall new Jacking oil manifold supplied by the customer. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-87 | 8.55.6.164 | Clean and replace jacking oil magnetic oil filter. | F | Contractor |  | In 2026 Overhaul | 35 | 140.1085 | 4903.7964 |  |  |  |  | 0
00173164/00001 | 28243985-88 | 8.55.6.165 | Remove and inspect vapour extraction fan internals and piping | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-89 | 8.55.6.166 | Visualy Inspect all inlet and oil take off pipes at tank for any leaks | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  |  | 0
00173164/00001 | 28243985-90 | 8.55.6.168 | Drain main oil tank of oil into tankers supplied by NRG. Empty date to be supplied by Contractor | F | Contractor |  | In 2026 Overhaul | 35 | 140.1085 | 4903.7964 |  |  |  |  | 0
00173164/00001 | 28243985-92 | 8.55.6.169 | Clean main oil tank (NRG to inspect after clean) | F | Contractor |  | In 2026 Overhaul | 74 | 140.1085 | 10368.0266 |  |  |  |  | 0
00173164/00001 | 28243985-93 | 8.55.6.180 | Remove and inspect main drain valve at main oil tank before oil goes back in. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28244079-08 | 8.55.6.172 | Install manufactured oil strainers for filtering turbine oil system during commissioning | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243985-95 | 8.55.6.181 | Overhaul turbine thrust oil assembly, replace change over valve orings. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243985-96 | 8.55.6.173 | Contractor to set up stream liner for filtering oil for a minimun of 10 days before oil curciut is put into service | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
|  |  | Remove TE upper endshield (Rescue squad to be on site and notified) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove fan baffles, bell housing, etc from TE end shield | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove compressor blower | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove oil & gas piping from end shields | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243978-01 | 8.56.6.001 | Remove exciter rotor, pilot exciter, coolers, bearing base, etc | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  |  | 0
00173164/00004 | 28243978-03 | 8.56.6.002 | Hand over the Exciter rotor to Contractor | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243978-04 | 8.56.6.004 | Clean and pressure test air coolers | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
|  |  | Insert Skid Plate and shoe (support rotor at TE) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243978-05 | 8.56.6.005 | Inspect and test coupling bolts, etc | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
|  |  | Unbolt and lower TE end shield (Floor removal policy to be in place) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install rear (coupling shoe support) and fan blade protection bracket | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove Rotor | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Inspection & Repairs | [5 empty] | 140.1085 |  |  | 26900.8258
|  | 8.56.6.030 | Generator H2 Seals (Inspection & Repairs) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243978-06 | 8.56.6.006 | Overhaul excitor rotor and stator | F | NRG Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243978-17 | 8.56.6.007 | Replace exciter rotor, Stator, pilot exciter, coolers, bearing base to correct specifications | F | Contractor |  | In 2026 Overhaul | 41 | 140.1085 | 5744.4472 |  |  |  |  | 0
00173164/00004 | 28243979-02 | 8.56.6.011 | Remove bearings 5 & 6 outer oil wipers and top support covers | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  |  | 0
00173164/00004 | 28243979-04 | 8.56.6.013 | Perform strip down measurements of bearings 5 & 6 & unbolt upper bearings | F | Contractor |  | In 2026 Overhaul | 45 | 140.1085 | 6304.881 |  |  |  |  | 0
00173164/00004 | 28243979-05 | 8.56.6.014 | Remove upper and lower bearings 5 & 6 | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  |  | 0
00173164/00004 | 28243979-07 | 8.56.6.016 | Undo LP-Gen Coupling and perform Coupling Alignment | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00004 | 28243979-08 | 8.56.6.017 | Remove outer oil wipers and top support frame | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  |  | 0
|  |  | Generator Rotor Inspection and testing of H2 up shaft lead seals. | [5 empty] | 140.1085 |  |  | 5604.3387
00173164/00004 | 28243979-09 | 8.56.6.018 | Remove H2 seal ring holders | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
|  |  | Arrival and set up of induction heating equipment | F | Contractor |  | Not required |  | 140.1085
|  |  | Electrical testing of the generator rotor prior to removal of the EE retaining ring | F | Contractor |  | Not required |  | 140.1085
|  |  | Reposition the generator rotor onto rollers | F | Contractor |  | Not required |  | 140.1085
|  |  | Set up and heating of the EE retaining ring | F | Contractor |  | Not required |  | 140.1085
|  |  | Remove EE Endbell (Endring) for H2 up shaft lead seal replacement | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT crack sensitive areas at the endring circlip groove, End ring and shrink fit area | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Cleaning of the EE retaining ring and shrink fit area | F | Contractor |  | Not required |  | 140.1085
|  |  | Remove and replace H2 up shaft lead seals | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Removal and replacement of the first set of slot for testing | F | Contractor |  | Not required |  | 140.1085
|  |  | Replace Exciter end Endbell and use new insulation | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Leak Test Generator rotor with nitrogen after H2 seals are replaced (350KPA) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove one nominated row of Generator fan blower blading for NDT testing | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | NDT blower section and fan blades/Rotor (test insitue blading) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Replace fan blades and fit closing blades to OEM specfications | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | If NDT report shows cracking in exciter end rotor circlip groove? (Decision to be made if Turb end End Ring is removed for NDT) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Generator End Shields | [5 empty] | 140.1085 |  |  | 2802.1694
|  |  | Remove lower end shields from foundations | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-10 | 8.56.6.019 | Remove bolts from inner labyrinths (EE) (EEnd only as we are only removing the top end shield for robot access) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  |  | 0
00173164/00004 | 28243979-11 | 8.56.6.020 | Reinstall bearings 5 & 6 (lower halves) | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  |  | 0
|  |  | Coolers | [5 empty] | 140.1085
|  |  | Inspect H2 Coolers (water side) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Steam clean H2 coolers | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Pressure test coolers (H2 ) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Stator Inspections | [5 empty] | 140.1085
|  |  | Robotic Inspection being performed on Stator and Rotor (Contractor to determine which tests are being performed by the Robot) |  |  |  | In 2026 Overhaul |  | 140.1085
00173164/00004 | 28243979-12 | 8.56.6.021 | Remove EE upper end shield only(Rescue squad required) | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00004 | 28243979-13 | 8.56.6.022 | Support rotor at EE (Install bracket and sling) | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  |  | 0
|  |  | Resin End Winding Treatment | [5 empty] | 140.1085
00173164/00004 | 28243979-14 | 8.56.6.023 | Remove bearing 6 | F | Contractor |  | In 2026 Overhaul | 14 | 140.1085 | 1961.5185 |  |  |  |  | 0
00173164/00004 | 28243979-01 | 8.56.6.024 | Unbolt and lower EE end shield (Floor removal policy to be in place) | F | Contractor |  | Check to see if this is required for robotic inspection (Contractor to determine scope) |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-15 | 8.56.6.026 | Remove bearing 5 | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  |  | 0
00173164/00004 | 28243979-17 | 8.56.6.031 | Clean H2 seal ring holders and measure (supply size to NRG) | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00004 | 28243979-18 | 8.56.6.032 | Rectify H2 Seal Holder (NRG) | F | Contractor |  | In 2026 Overhaul | 7 | 140.1085 | 980.7593 |  |  |  |  | 0
|  |  | HV Testing | [5 empty] | 140.1085
|  |  | NRG electricians will work in with Contractor to carry out the below testing | [5 empty] | 140.1085
Robotic Inspection being performed on Stator and Rotor (Contractor to determine which tests are being performed by the Robot)
00173164/00004 | 28243979-19 | 8.56.6.033 | Machine new H2 seals | F | NRG |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-20 | 8.56.6.034 | Measure new seal rings and check fittment | F | Contractor |  | In 2026 Overhaul | 26 | 140.1085 | 3642.8202 |  |  |  |  | 0
00173164/00004 | 28243979-21 | 8.56.6.035 | Replace inner labyrinths seal strips if required | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00004 | 28243979-22 | 8.56.6.036 | Machine inner labyrinths (only inspecting EE inner labyrinth) | F | NRG |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-23 | 8.56.6.037 | Prepare new insulation package (Holes have to be drilled in OEM supplied gaskets) | F | Contractor |  | In 2026 Overhaul | 104 | 140.1085 | 14571.2806 |  |  |  |  | 0
00173164/00004 | 28243979-03 | 8.56.6.038 | When the Exciter shaft is removed, Contractor to perform air leak test on Generator shaft with pressure plare (report findings toNRG Engineering) | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00004 | 28243979-24 | 8.56.6.048 | Clean end shields & check mating surfaces (only perform this operation at EE) | F | Contractor |  | Clean for reinstallation of top end shield | 80 | 140.1085 | 11208.6774 |  |  |  |  | 0
00173164/00004 | 28243979-25 | 8.56.6.049 | Blue Checking of Bottom Sphericals on Bearing's 5 & 6 | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  |  | 0
|  |  | 9.Stator Winding AC High Potential Test (Test voltage 24kV) |  |  |  | Not required |  |  | 0 |  |  |  |  | 0
|  |  | 10.Rotor Winding AC High Potential Test (Test voltage 1kV) |  |  |  | Not required |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-26 | 8.56.6.053 | Stator Fact Finding Visual Inspection | F | NRG |  | NRG Engineering |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-27 | 8.56.6.054 | Stator inspection performed by Contractor engineering (Contractor to define scope being performed with Robot) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-28 | 8.56.6.055 | Preparation | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-29 | 8.56.6.056 | Cleaning Endwinding & Mask areas | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-30 | 8.56.6.057 | Heating | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-31 | 8.56.6.058 | Treat overhang with Resin | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | 17. Full flux test on the stator core | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reassembly / Generator and Exciter | [5 empty] | 140.1085 |  |  | 0
00173164/00004 | 28243979-32 | 8.56.6.059 | Finalise Works | O | Contractor |  | Only if required, has been completed on all units, as a variation. |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Reposition lower end shields / Prepare temporary floor removal area | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Insert Skid plate and final clean for rotor installation | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install Rotor Shoe and Insertion Devices | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Insert rotor & support rotor at exciter end | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install Lower Endshield Turbine Side and support Rotor | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Remove Skid Plate | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install Lower Exciter End Shield | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install oil pipework for Jacking Oil & Bearing pipework | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-34 | 8.56.6.060 | 1.Winding Resistance measurement – stator | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-35 | 8.56.6.061 | 2.Insulation Test & Polarization Index - stator | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-36 | 8.56.6.062 | 3.DC Controlled Over-voltage Tests - stator | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
|  |  | Assemble Hydrogen Blower (TE) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install Baffles and plates in H2 cooler area and tab over | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install TE Upper Endshield (Rescue squad to be on site and notified) | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-37 | 8.56.6.063 | 4.Dielectric Dissipation Factor and Capacitance testing - stator | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-38 | 8.56.6.064 | 5.Partial Discharge testing of the stator winding (Test gear should be capable of carring out PD on phases at the same time) | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-39 | 8.56.6.065 | 6.RSO testing - rotor | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-40 | 8.56.6.066 | 7.Insulation Resistance – rotor | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-41 | 8.56.6.067 | 8.Winding Resistance – rotor | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-42 | 8.56.6.070 | 11.RTDs Test – (Resistance Test & Insulation Test) | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-43 | 8.56.6.071 | 12.Rotor Inspection | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
|  |  | Measure and set fan blower clearance | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Install H2 coolers | F | Contractor |  | Not required |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-44 | 8.56.6.072 | 13.Stator Inspection | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-45 | 8.56.6.073 | 14.Slot Wedge Deflection Test | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
|  |  | Bearings (5,6 & 7) | [5 empty] | 140.1085 |  |  | 1961.5185
00173164/00004 | 28243979-46 | 8.56.6.074 | 15.Bump Test (Stator end windings) | F | Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00004 | 28243979-06 | 8.56.6.076 | Remove the clean condition tents & store | F | Contractor |  | In 2026 Overhaul | 0 | 140.1085 | 0 |  |  |  |  | 0
00173164/00004 | 28243979-48 | 8.56.6.086 | Insert bearings 5 & 6 (lower halves) | F | Contractor |  | In 2026 Overhaul | 14 | 140.1085 | 1961.5185 |  |  |  |  | 0
|  |  | Oil Labyrinths (5,6 & 7) |  | Contractor |  |  |  | 140.1085 |  |  | 7565.8573
00173164/00004 | 28243979-49 | 8.56.6.087 | Install air gap seal (Exciter End) | F | Contractor |  | In 2026 Overhaul | 24 | 140.1085 | 3362.6032 |  |  |  |  | 0
00173164/00004 | 28243979-50 | 8.56.6.088 | Install upper Ends Shield Exciter End (Rescue Squad) | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
|  |  | H2 Seal Oil System | [5 empty] | 140.1085 |  |  | 94713.3242
00173164/00004 | 28243979-51 | 8.56.6.092 | Install inner labyrinths (EE only as other end is not being disassembled) | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00004 | 28243979-53 | 8.56.6.094 | Complete tightening of inner labyrinths | F | Contractor |  | EEnd only | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00004 | 28243979-54 | 8.56.6.095 | Pump sealant through end shields | F | Contractor |  | EEnd only | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00004 | 28243979-55 | 8.56.6.096 | Remove bearings 5 & 6 | F | Contractor |  | In 2026 Overhaul | 12 | 140.1085 | 1681.3016 |  |  |  |  | 0
00173164/00004 | 28243979-56 | 8.56.6.097 | Install H2 Seal (First Set) | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00004 | 28243979-57 | 8.56.6.098 | Install H2 Seal (Second Set) | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00004 | 28243979-58 | 8.56.6.101 | Complete bearing cover preliminary installation (For megger check) | F | Contractor |  | In 2026 Overhaul | 38 | 140.1085 | 5324.1218 |  |  |  |  | 0
00173164/00004 | 28243979-59 | 8.56.6.102 | Air pressure test to OEM specifications | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243986-23 | 8.56.6.103 | Clean, inspect and carry out measurement survey on bearings | F | Contractor |  | In 2026 Overhaul | 75 | 140.1085 | 10508.1351 |  |  |  |  | 0
00173164/00001 | 28243986-09 | 8.56.6.104 | NDT Bearing's 5,6 & 7 | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243986-24 | 8.56.6.105 | Clean bearings after NDT testing | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243986-25 | 8.56.6.106 | Replace brass sealing strips where required | F | Contractor |  | In 2026 Overhaul | 75 | 140.1085 | 10508.1351 |  |  |  |  | 0
00173164/00001 | 28243986-26 | 8.56.6.107 | Machine oil labyrinths | F | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243982-17 | 8.56.6.108 | Inspect AC and DC oil pump non return valves. | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243982-18 | 8.56.6.109 | Remove AC / DC pump motors, for electricians to Overhaul | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243982-19 | 8.56.6.110 | Remove and replace AC and DC seal oil pumps with refurbished pumps. | F | Contractor |  | In 2026 Overhaul | 18 | 140.1085 | 2521.9524 |  |  |  |  | 0
00173164/00001 | 28243982-46 | 8.56.6.111 | Replace and align AC and DC Overhauled electric motors | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243982-20 | 8.56.6.112 | Clean all strainers on seal oil system. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243982-21 | 8.56.6.113 | Inspect and clean main and intermediate seal oil tanks. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243982-22 | 8.56.6.114 | Inspect main seal oil float valve and seat. | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  |  | 0
00173164/00001 | 28243982-23 | 8.56.6.115 | Inspect intermediate seal oil float valve and seat. | F | Contractor |  | In 2026 Overhaul | 15 | 140.1085 | 2101.627 |  |  |  |  | 0
00173164/00001 | 28243982-24 | 8.56.6.116 | Inspect and repair hydrogen drier isolation valves. – ST13-S501 and ST13-S507 | F | Contractor |  | In 2026 Overhaul | 4 | 140.1085 | 560.4339 |  |  |  |  | 0
00173164/00001 | 28243982-25 | 8.56.6.117 | Inspect and repair hydrogen valves – ST11-S501, ST11-S502, ST11-S516, ST11-S517, ST11-S520, ST11-S521 and ST11-S525.S589 | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243982-26 | 8.56.6.118 | Inspect and repair seal oil valves – SU11-S596, SU11-S597, SU11-598, SU11-S599, SU14 – S510, SU14– S511, SU14 – S512, SU14 – S513, SU14 – S514, SU14 – S515. | F | Contractor |  | In 2026 Overhaul | 43 | 140.1085 | 6024.6641 |  |  |  |  | 0
00173164/00001 | 28243982-27 | 8.56.6.119 | Inspect and repair hydrogen valves – ST12-S522, S521, S529. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
|  |  | Hydrogen Seal Oil Plant – After Oil Flush | [5 empty] | 140.1085 |  |  | 2802.1694
00173164/00001 | 28243982-28 | 8.56.6.120 | Inspect and repair CO2 relief valves, (hi and low pressure, replace with new) | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243982-29 | 8.56.6.121 | Inspect and replace diaphragm on H2 analyzer regulator (large and small reg) Please measure for future diaphram sizing, report sizing to NRG Engineering | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
|  |  | Turbine Bearings & Couplings | [5 empty] | 140.1085
|  |  | Disassembly | [5 empty] | 140.1085 |  |  | 19895.4024
00173164/00001 | 28243982-30 | 8.56.6.122 | Inspect and replace diaphrams in H2 fill station pressure reducer valves- 3 off (ST12- N523, N524, N531). Please measure for future diaphram sizing, report sizes of diaphram to NRG Engineering. | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
00173164/00001 | 28243982-31 | 8.56.6.123 | Replace all seal oil pipework gaskets. | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243982-32 | 8.56.6.124 | Inspect generator liquid detection sight glass and replace gaskets. | F | Contractor |  | In 2026 Overhaul | 5 | 140.1085 | 700.5423 |  |  |  |  | 0
00173164/00001 | 28243982-33 | 8.56.6.125 | Inspect liquid level detection valves SP11-533, SP11-531, SP11-532, SP11-539, SP11-501, SP11-534 | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243982-34 | 8.56.6.126 | Inspect and replace seal oil cooler top “O” rings. Pressure test seal oil coolers to specification. | F | Contractor |  | In 2026 Overhaul | 30 | 140.1085 | 4203.254 |  |  |  |  | 0
00173164/00001 | 28243982-35 | 8.56.6.127 | Inspect, flush and clean all hydrogen vent pipework. | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243982-36 | 8.56.6.128 | Visually inspect all hydrogen pipework, manifold and clamps to check for wear or leaks. | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243982-37 | 8.56.6.129 | Inspect, flush and clean bearing vapour extraction fan (AVR floor). | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243982-38 | 8.56.6.130 | Replace all valves locking spacers and fixing chains. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243982-39 | 8.56.6.131 | Change out A and B valves with Overhauled valves provided from NRG store | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
|  |  | Perform coupling concentricity checks (HP-IP, IP-LP, LP-Gen) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28244079-07 | 8.56.6.132 | Commission A and B valves to correct pressure settings. | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243982-49 | 8.56.6.133 | Inspect main seal oil float valve and seat (have NRG Turbine inspector inspect seat) | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
|  |  | Remove coupling bolts from HP/IP, IP/LP couplings | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Perform coupling alignments (MOP, HP-IP, IP-LP) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Inspection | [5 empty] | 140.1085 |  |  | 9667.4843
00173164/00001 | 28243982-50 | 8.56.6.134 | Inspect intermediate seal oil float valve and seat for debris(have NRG turbine inspector inspect seat) | F | Contractor |  | In 2026 Overhaul | 13 | 140.1085 | 1821.4101 |  |  |  |  | 0
00173164/00001 | 28243986-02 | 8.55.6.180 | Disconnect and remove the instrumentation from the turbine bearings pedestals |  | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243986-05 | 8.55.6.182 | Disconnect and remove the internal instrumentation from the bearings |  | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243986-06 | 8.55.6.183 | Measure the thrust bearing axial clearance | F | Contractor |  | In 2026 Overhaul | 16 | 140.1085 | 2241.7355 |  |  |  |  | 0
00173164/00001 | 28243986-07 | 8.55.6.185 | Record axial & radial positions of the turbine rotors to the turbine casings and bearing pedestals prior to bearing removal | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
|  |  | Automatic barring gear (if not already fitted) | [5 empty] | 140.1085 |  |  | 7635.9115
00173164/00001 | 28243986-11 | 8.55.6.186 | Measure and record HP & IP casing to rotor roll out check | O | Contractor |  | Only if required | 24 | 140.1085 | 3362.6032 |  |  |  |  | 0
00173164/00001 | 28243986-10 | 8.55.6.187 | Remove lower thrust bearing and remove thrust pads | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243986-13 | 8.55.6.188 | Install thrust bearing and perform axial clearance checks on HP/IP rotors coupled | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
|  |  | Bearing pedestal Foundation bolt hydraulic tensioning, | [5 empty] | 140.1085
|  |  | Bearing 1 Foundation Bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Bearing 2 Foundation Bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Bearing 3 Foundation Bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Bearing 4 Foundation Bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Generator Foundation Bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Exciter Foundation Bolts | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Measure all pedestal base plate movement where possible while hydraulic tightening pedestals, record and evaluate these measurements in case further coupling alignment adjustments are needed | V | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | Assembly | [5 empty] | 140.1085 |  |  | 23608.2768
00173164/00001 | 28243986-12 | 8.55.6.189 | Reinstall with 2 thrust pads fitted | F | Contractor |  | In 2026 Overhaul | 8 | 140.1085 | 1120.8677 |  |  |  |  | 0
|  |  | Hone HP and IP Rotor's to accept new coupling bolt sizing. | F | Contractor |  | In 2026 Overhaul |  | 140.1085
|  |  | Perform coupling alignments (MOP, HP-IP, IP-LP) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
|  |  | MOP, HP-IP and IP-LP Coupling Alignment Adjustments | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243986-14 | 8.55.6.191 | Perform Stub Shaft Runout | F | Contractor |  | In 2026 Overhaul | 10.5 | 140.1085 | 1471.1389 |  |  |  |  | 0
00173164/00001 | 28243986-15 | 8.55.6.192 | Remove windage plates from all couplings | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  |  | 0
00173164/00001 | 28243986-18 | 8.55.6.195 | Remove all lower turbine bearings for visual inspection on disessembly | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243986-30 | 8.55.6.196 | NDT all bearings and thrust pads | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243986-28 | 8.55.6.199 | Machine oil labyrinths to nominated sizes as required |  | NRG |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
|  |  | Remove bearing covers 1 - 4 and carry out a post oil flush clean and inspection | F | Contractor |  | Utilize best method of oil flushing for Unit 2 in 2026 |  | 140.1085 | 0
00173164/00001 | 28243985-91 | 8.55.6.201 | Contractor Test fit new modifided barring gear | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243986-29 | 8.55.6.101 | Install all the lower turbine bearings and connect lift oil hoses | F | Contractor |  | In 2026 Overhaul | 25 | 140.1085 | 3502.7117 |  |  |  |  | 0
00173164/00001 | 28243986-33 | 8.55.6.102 | Tighten all couplings and perform concentricity checks | F | Contractor |  | In 2026 Overhaul | 45 | 140.1085 | 6304.881 |  |  |  |  | 0
00173164/00001 | 28243986-34 | 8.55.6.103 | Measure and record all the bearing pedestal radial and axial references (on completion of casing rollouts | F | Contractor |  | In 2026 Overhaul | 35 | 140.1085 | 4903.7964 |  |  |  |  | 0
|  |  | Final Coupling Alignments & Bearing Closure | [5 empty] | 140.1085 |  |  | 76148.9522
00173164/00001 | 28243986-35 | 8.55.6.104 | Install and set the oil wipers | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243986-43 | 8.55.6.106 | Perform oil flushing with strainers on flushing pipes | F | Contractor |  | Utilize best method of oil flushing for Unit 2 in 2026 | 60 | 140.1085 | 8406.5081 |  |  |  |  | 0
00173164/00001 | 28243986-44 | 8.55.6.107 | Final assembly of turbine bearings & bearing bridges including clearance checks | F | Contractor |  | In 2026 Overhaul | 50 | 140.1085 | 7005.4234 |  |  |  |  | 0
00173164/00001 | 28243986-46 | 8.55.6.109 | Final assembly of the bearing pedestals | F | Contractor |  | In 2026 Overhaul | 63.5 | 140.1085 | 8896.8877 |  |  |  |  | 0
00173164/00001 | 28243986-36 | 8.55.6.111 | Pressurise Generator for LP- Gen Coupling alignment- 100Kpa-350Kpa | F | NRG/Contractor |  | In 2026 Overhaul |  |  | 0 |  |  |  |  | 0
00173164/00001 | 28243986-37 | 8.55.6.112 | Complete bearing cover preliminary installation (For megger check) | F | Contractor |  | In 2026 Overhaul |  | 140.1085 | 0 |  |  |  |  | 0
00173164/00001 | 28243986-38 | 8.55.6.113 | Perform coupling alignment readings of LP to Generator Rotor | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243986-39 | 8.55.6.114 | Adjust stator to correct alignment | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243978-20 | 8.55.6.117 | Reinstall exciter Rotor | F | Contractor |  | In 2026 Overhaul | 80 | 140.1085 | 11208.6774 |  |  |  |  | 0
00173164/00001 | 28243986-40 | 8.55.6.118 | Perform Gen-Exc Coupling Alignment, tighten coupling bolts and perform concentricity check, install windage plates. | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243986-41 | 8.55.6.119 | Air pressure test (24 hour pressure test) | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243986-54 | 8.55.6.121 | Fully assemble bearings & covers | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
00173164/00001 | 28243986-55 | 8.55.6.123 | Prepare No. 5 and 6 bearings for oil flushing | F | Contractor |  | In 2026 Overhaul | 20 | 140.1085 | 2802.1694 |  |  |  |  | 0
00173164/00001 | 28243986-56 | 8.55.6.124 | Prepare No.7 bearing for oil flushing | F | Contractor |  | In 2026 Overhaul | 10 | 140.1085 | 1401.0847 |  |  |  |  | 0
00173164/00001 | 28243978-18 | 8.55.6.125 | Install, pilot exciter, coolers, etc. | F | Contractor |  | In 2026 Overhaul | 40 | 140.1085 | 5604.3387 |  |  |  |  | 0
|  |  | NDT Required, "Separate spread sheet outlining NDT for Turbine and Genrator" for 2024 | [5 empty] | 140.1085
|  |  | Refer to NDT document and document numbering system | [5 empty] | 140.1085
|  |  | HP Steam Turbine Admission Pipework, Valves and Strainer | [5 empty] | 140.1085
|  |  | IP Admission Piping, Valves and Strainers | [5 empty] | 140.1085
|  |  | Generator Rotor NDT- NDT document produced by NRG Electrical Engineering | [5 empty] | 140.1085
|  |  | General | [5 empty] | 140.1085
|  |  | General/indirect labour (to be used for variations, etc.) | F | Contractor |  |  |  | 140.1085 | 0 |  |  |  |  | 0
[7 empty] | TOTAL hrs | 5952 | 140.1085 | 833925.6 |  | 781945.3585 | 0 | #DIV/0! | 0 | 0 | [24 empty] | 0 | 0 | 0 |  |  |  | 0
Legend
F = Fixed
V = Variable
O = Optional
Note on H64: Author: Separate out the costs as stage 1 ,2 and 3 in the TCE as if we where installing all 3 blade stages, we need to know what to expect with these costs, I do not believe we will find cracking in stages 2 and 3.
Note on H65: Author: show costs for machining all 3 stages, but separate it out in the TCE. As stage 1 , 2 and 3
Note on M640: Mustapha, Isa: SEAG

## Variations
Service Order Number/Release | Work Order | Activity description | Estimated Hours | Gang rate $/hr | Estimated Total Cost (including Overhead & Profit) | Approved / Not Approved / Pending | Estimate/QTY Comment | Week 1 - Actual Hours | Week 1 - Actual Total Cost | Week 2 - Actual Hours | Week 2 - Actual Total Cost | Week 3 - Actual Hours | Week 3 - Actual Total Cost | Week 4 - Actual Hours | Week 4 - Actual Total Cost | Week 5 - Actual Hours | Week 5 - Actual Total Cost | Week 6 - Actual Hours | Week 6 - Actual Total Cost | Week 7 - Actual Hours | Week 7 - Actual Total Cost | Week 8 - Actual Hours | Week 8 - Actual Total Cost | Week 9 - Actual Hours | Week 9 - Actual Total Cost | Week 10 - Actual Hours | Week 10 - Actual Total Cost | Week 11 - Actual Hours | Week 11 - Actual Total Cost | Week 12 - Actual Hours | Week 12 - Actual Total Cost | Total - Actual Hours | Total - Actual Total Cost | Percentage of Hours Complete | Percentage of Cost Used | Task Complete | Forecast Cost for Completion of Project
|  | Variation 001 - Description |  |  | 0 | [26 empty] | 0 | 0 | #DIV/0! | #DIV/0! | No | 0
|  |  | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!

## Overhaul rates
Code | Description | Rate | UOM | FULL DESCRIPTION

## Invoices-receipts
Scope No. | NRG Service Order | Date | Week Ending | Start Date | End Date | No | Supplier | Chargeable | Scope | Name / Rego No. | Cost | Gross Margin | Sell |  | Claim No. | Comments
90.4 | #REF! | 2026-05-01 | 2026-05-14 | 2026-05-01 | 2026-05-14 | 1 | ABC Hotel | Yes | Accommodation | John Smith | 1200 | 1% | 1212.1212 | 1212.1212 |  | Example
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Invoice Summary
|  | WE 17-May-26 | WE 31-Apr-26
Service Order and Release Number | Prepayment | Invoice 1 | Invoice 2 | Invoice 3 | Invoice 4 | Invoice 5 | Invoice 6 | Invoice 7 | Progress Invoice Total
TasTK - Overheads labour and Skilled Labour
Contract Number - 00173164/000001
Contract Number - 00173164/000003
Contract Number - 00173164/000004
0
Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Non TasTK - Overheads
Contract Number - 00173164/000002
Contract Number - 00173164/000002 EURO
0
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All excluding GST.

## KPI Model
Actual Cost % of Adjusted Cost | Actual Cost Included in KPI | Incentive / Disincentive Percentage | Incentive / Disincentive | Notes
90% | 0 | 5% | 0 | Where cost is less than 90%, the incentive payment at 90% is applicable.
91% | 0 | 4% | 0 | Incentive
92% | 0 | 3% | 0 | Incentive
93% | 0 | 2% | 0 | Incentive
94% | 0 | 1% | 0 | Incentive
95% | 0 | 0% | 0 | Deadband
96% | 0 | 0% | 0 | Deadband
97% | 0 | 0% | 0 | Deadband
98% | 0 | 0% | 0 | Deadband
99% | 0 | 0% | 0 | Deadband
100% | 0 | 0% | 0 | Deadband
101% | 0 | 0% | 0 | Deadband
102% | 0 | 0% | 0 | Deadband
103% | 0 | 0% | 0 | Deadband
104% | 0 | 0% | 0 | Deadband
105% | 0 | 0% | 0 | Deadband
106% | 0 | -1% | 0 | Disincentive
107% | 0 | -2% | 0 | Disincentive
108% | 0 | -3% | 0 | Disincentive
109% | 0 | -4% | 0 | Disincentive
110% | 0 | -5% | 0 | Actual capped at 110% of KPI costs, no further cost to Principal.
Key Performance Indicators |  |  |  |  | Definitions | Notes
Key Performance Item | Minimum Expectation | 1 LTI / RWDI | 2 or more LTI / RWDI |  | Lost Time Injury (LTI) is in accordance with AS1885. Restricted Work Day Injury (RWDI) - an occupational injury where, as a result: - the employee was assigned to another job on a temporary basis; or - the employee worked at a permanent job less than full time; or - the employee worked at his or her permanently assigned job but could not perform all the duties normally connected with it. For sake of clarity and for the purpose of the Contract, a Restricted Work Day Injury is a significant injury, determined as such by a medical practitioner. Medical Treatment Case (MTC) is one where treatment was received by a Medical/Allied Health Practitioner. Medical Treatment includes administration of prescription medication; the use of wound closing devices such as sutures or staples; the use of devices with rigid stays or other systems designed to immobilise parts of the body; the use of physical therapy or chiropractic treatment; and the use of eye patches (except as a precautionary measure). Medical Treatment does not include visits to a physician or other licensed health care professional solely for observation or counselling, diagnostic procedures such as x-rays or blood tests; administration of prescription medications used solely for diagnostic purposes (Eg. eye drops to dilate pupils) or as a single dose administered on a first visit for a minor injury or discomfort. Notifiable Incident is one which is notifiable to the DES. | 1. The impact of Safety, Environment, Quality and Schedule KPI's is cumulative. Eg. 1 MTC and 1 Environmental Notifiable Incident is cumulative resulting in a reduction by 2%. 2. The impact of multiple KPI breaches along the same KPI is not cumulative. Eg. 2 MTC Incidents is not cumulative from 1 MTC and results in a reduction by 2%. 3. Incentive Payment is achieved by underrun of the Actual KPI Cost <5%, applicable linearly an incentive payment upto 5% from 94% to 90%. 4. Disincentive is achieved by overrun of the Actual KPI Cost >5%, applicable linearly a reduction of upto 5% from 105% to 110%. 5. Variations do not form part of the TCE, Variation work to be completed at mutually agreed schedule of rates or fixed price. 6. Only labour from overheads and skilled labour are included in the KPI. Other Overheads and Equipment costs excluded from the KPI are priced as a 'capped estimate'.
Safety | Zero Harm | Reduction by 2% + No Incentive Payment | Show Cause Notice + 5% Reduction + No Incentive Payment
|  | 1 MTC | 2 MTC | 3 or more MTC
|  | Reduction by 1% + No Incentive Payment | Reduction by 2% + No Incentive Payment | Show Cause Notice + 5% Reduction + No Incentive Payment
Environment | Zero Incidents | 1 Notifiable Incident | 2 or more Notifiable Incidents
|  | Reduction by 1% + No Incentive Payment | Show Cause Notice + 5% Reduction + No Incentive Payment
Quality | 100% compliance | Failures - Rework at no cost to the Principal. Payment for the task on hold until 100% compliance is achieved. Failure, as determined by the Principal's issue/acceptance of an Non Conformance Report (NCR), that leads to Loss of Availability (LOA) commencing from the start of the commissioning period to the end of the Defects Liability period will incur a 1% reduction in profit for each occurrence.
Schedule | 100% compliance | Delays beyond the Practical Completion Date or delays to critical milestone dates will attract Liquidated Damages.

## TAStK
TIME SHEET
| FIRST LAST | NNNNNNNN | NNN | NNNNNNNN-NNNNN | NNNNNNN-NN | DD/MM/YYYY | HH:MM
| Contractor Name | Employee Number | Position | Contract | Work Order Number-Task | Date | Hours Worked | Contractor Codes
| EMP_NAME | EMP_NO | POSITION | CONTRACT | WO_NO-TASK | DATE | HOURS | Contractor Codes
Example |  | 116 | 173164-PROJMGR-T1.0 | 173164-0001 |  | 2024-04-23 | 3